## Losses Tool
WS1A Losses Tool
| Requirements Information |  |  |  |  | Convert from KW &Hrs to MWh
| Licence Area | NORW |  |  |  | This calculator helps to convert kW into MWh
| Period | Winter Daytime |  |  |  | kW | Hrs | MWhs
| Requirement Voltage | HV Substation |  |  |  | 720 | 48 | 34.56
| Requirement Capacity (MWh) | -34.56 | +Ve for a demand increase (Export decrease) - Ve for a demand decrease (Export increase) |  |  | Note:the output of this calculator does not link to the rest of the sheets functionality
MWh
|  | LV Network | LV Substation | HV Network | HV Substation | EHV Network
| Flexibility Required | 0 | 0 | 0 | -34.56 | 0
Winter
Night
Other
[9 empty] | Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Flexibility Provided | [8 empty] | Winter Peak | Winter Daytime | Night | Other
| Please complete this section with details of the type of service you are looking to/have procured. The total flexiblity provided must be equal to the service requirement in MWh | [7 empty] | Monday to Friday March to October | 0 | 0 | 00:00 - 07:00 | 07:00 - 00:00
| Flexibility provided Voltage category | Generation Export Increase (MWh) | Demand Increase (MWh) | Demand Reduction (MWh) | Generation Export Reduction (MWh) |  |  |  | Monday to Friday November to February | 16:00 – 19:00 | 07:00 – 16:00 19:00 – 00:00 | 00:00 - 07:00 | 0
| LV Network |  |  | 34.56 |  |  |  |  | Saturday and Sunday All Year | 0 | 0 | 00:00 - 07:00 | 07:00 - 00:00
LV Substation
HV Network
HV Substation
EHV Network
Additional Functionality
| Will demand reduction need to increase production post service provision | Yes
| Electricity storage system providing generation output | No
Losses Total
Total Losses (Green if negative/reduced)
-0.41472
Page Notes:
Yellow Boxes can be input with data
| Grey boxes should not contain any data | [12 empty] | Data Table
| Green Boxes have been completed but can still be edited | [13 empty] | SWEB |  |  |  | SWAE |  |  |  | MIDE |  |  |  | EMEB |  |  |  | NORW |  |  |  | SEPD |  |  |  | SHEPD |  |  |  | Manweb |  |  |  | SPD |  |  |  | LPN |  |  |  | SPN |  |  |  | EPN |  |  |  | NPG Y |  |  |  | NPG NE
[14 empty] | LLFs | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5
[14 empty] | 132kV | 1.002 | 1.001 | 1.001 | 1.001 | 1.009 | 1.008 | 1.006 | 1.007 | 1.002 | 1.002 | 1.002 | 1.002 | 1.003 | 1.003 | 1.002 | 1.002 | 1.009 | 1.008 | 1.006 | 1.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | EHV Network | 0.012 | 0.013 | 0.011 | 0.013 | 0.015 | 0.016 | 0.016 | 0.016 | 0.013 | 0.012 | 0.009 | 0.01 | 0.011 | 0.011 | 0.01 | 0.011 | 0.01 | 0.01 | 0.009 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | HV Substation | 0.006 | 0.005 | 0.006 | 0.006 | 0.008 | 0.007 | 0.008 | 0.007 | 0.007 | 0.007 | 0.006 | 0.007 | 0.006 | 0.006 | 0.007 | 0.006 | 0.005 | 0.005 | 0.006 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | HV Network | 0.018 | 0.016 | 0.011 | 0.013 | 0.009 | 0.008 | 0.002 | 0.006 | 0.026 | 0.023 | 0.013 | 0.018 | 0.016 | 0.014 | 0.008 | 0.011 | 0.011 | 0.009 | 0.006 | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | LV Substation | 0.014 | 0.016 | 0.023 | 0.018 | 0.018 | 0.018 | 0.025 | 0.02 | 0.018 | 0.019 | 0.025 | 0.02 | 0.011 | 0.013 | 0.021 | 0.016 | 0.013 | 0.015 | 0.02 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | LV Network | 0.015 | 0.012 | 0.01 | 0.011 | 0.018 | 0.015 | 0.01 | 0.013 | 0.017 | 0.014 | 0.01 | 0.013 | 0.031 | 0.026 | 0.017 | 0.021 | 0.045 | 0.038 | 0.026 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | Time periods | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 1 | Period 2 | Period 3 | Period 4 | Period 5
[15 empty] | Peak | Winter | Night | Other | Peak | Winter | Night | Other | Peak | Winter | Night | Other | Peak | Winter | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Winter Peak | Winter Daytime | Night | Other | Extra
|  |  |  | Demand increase/Generation Export Increase | [5 empty] | Demand decrease/Generation Export Reduction |  |  |  | Monday to Friday March to October | 0 | 0 | 00:00 - 06:30 23:30 - 24:00 | 06:30 - 23:30 | 0 | 0 | 00:30 - 07:30 | 00:00 - 00:30 07:30 - 24:00 | 0 | 0 | 00:30 – 07:30 | 07:30 – 00:30 | 0 | 0 | 00:30 – 07:30 | 07:30 – 00:30 | 0 | 0 | 00:00 - 07:00 | 07:00 - 00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LV Network | LV Substation | HV Network | HV Substation | EHV Network |  |  | LV Network | LV Substation | HV Network | HV Substation | EHV Network | Monday to Friday November to February | 16:00 - 19:00 | 06:30 - 16:00 | 00:00 - 06:30 23:30 - 24:00 | 19:00 - 23:30 | 16:00 – 19:00 | 07:30 – 16:00 | 00:30 - 07:30 | 00:00 - 00:30 19:00 - 24:00 | 16:00 – 19:00 | 07:30 – 16:00 19:00 – 20:00 | 00:30 – 07:30 | 20:00 – 00:30 | 16:00 – 19:00 | 07:30 – 16:00 19:00 – 20:00 | 00:30 – 07:30 | 20:00 – 00:30 | 16:00 – 19:00 | 07:00 – 16:00 19:00 – 00:00 | 00:00 - 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV Network | 0 | 0 | 0 | 0 | 0 |  | LV Network | 0 | 0 | 0 | -2.9376 | 0 | Saturday and Sunday All Year | 0 | 0 | 00:00 - 06:30 23:30 - 24:00 | 06:30 - 23:30 | 0 | 0 | 00:30 - 07:30 | 00:00 - 00:30 07:30 - 24:00 | 0 | 0 | 00:30 – 07:30 | 07:30 – 00:30 | 0 | 0 | 00:30 – 07:30 | 07:30 – 00:30 | 0 | 0 | 00:00 - 07:00 | 07:00 - 00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV Substation | N/A | 0 | 0 | 0 | 0 |  | LV Substation | N/A | 0 | 0 | 0 | 0
Flexibility Provided | HV Network | N/A | N/A | 0 | 0 | 0 |  | HV Network | N/A | N/A | 0 | 0 | 0 |  | Period 3: NORW
| HV Substation | N/A | N/A | N/A | 0 | 0 |  | HV Substation | N/A | N/A | N/A | 0 | 0 |  | Period 2: LLFs; Period 3: Winter Peak; Period 4: Winter Daytime; Period 1: Night; Period 2: Other; Period 2: 132kV; Period 3: EHV Network; Period 4: HV Substation; Period 1: HV Network; Period 2: LV Substation; Period 3: LV Network
| EHV Network | N/A | N/A | N/A | N/A | 0 |  | EHV Network | N/A | N/A | N/A | N/A | 0 |  | Period 2: 132kV; Period 3: 1.009; Period 4: 1.008; Period 1: 1.006; Period 2: 1.007; Period 1: Winter Peak; Period 2: 1.009; Period 3: 0.01; Period 4: 0.005; Period 1: 0.011; Period 2: 0.013; Period 3: 0.045
[16 empty] | EHV Network | 0.01 | 0.01 | 0.009 | 0.01 | [6 empty] | Winter Daytime | 1.008 | 0.01 | 0.005 | 0.009 | 0.015 | 0.038
[16 empty] | HV Substation | 0.005 | 0.005 | 0.006 | 0.005 | [6 empty] | Night | 1.006 | 0.009 | 0.006 | 0.006 | 0.02 | 0.026
[16 empty] | HV Network | 0.011 | 0.009 | 0.006 | 0.008 | [6 empty] | Other | 1.007 | 0.01 | 0.005 | 0.008 | 0.015 | 0.034
[16 empty] | LV Substation | 0.013 | 0.015 | 0.02 | 0.015
[16 empty] | LV Network | 0.045 | 0.038 | 0.026 | 0.034
LLF Factors for Selected period
| Error Checking |  |  |  |  | Loss Increase on Upstream due to ESS charging |  |  | Loss Increase on Upstream due to DSR Shifting | [5 empty] | Period 2: 132kV; Period 3: 1.008
| LV network requirements error check | OK | [12 empty] | Period 2: EHV Network; Period 3: 0.01
| LV Substation requirements error check | OK |  |  |  | 1 |  |  | 1 | [5 empty] | Period 2: HV Substation; Period 3: 0.005
| HV network requirements error check | OK |  |  | EHV Network | 0 |  | EHV Network | 0 | [5 empty] | Period 2: HV Network; Period 3: 0.009
| HV Substation requirements error check | OK |  |  | HV Substation | 0 |  | HV Substation | 0 | [5 empty] | Period 2: LV Substation; Period 3: 0.015
| Procurement: | OK |  |  | HV Network | 0 |  | HV Network | 0 | [5 empty] | Period 2: LV Network; Period 3: 0.038
| Period | OK |  |  | LV Substation | 0 |  | LV Substation | 0
| Licence info check | OK |  |  | LV Network | 0 |  | LV Network | 2.5229
Winter Peak
Note on C5: Select the licence area you are operating within
Note on C6: Choose the period which you would like the service to operate within
Note on C7: Choose the Voltage where the constaint is being procured for.
Note on C8: Evans, Keith: Input the requirement in MWh
Note on C30: This function if selected "Yes" will calculate the losses associated with increasing site demand during the period with the lowest LLF. E.g a factory reduces production to provide a flexible service, following completion of the demand response delivery the site will increase production during non service delivery periods to make up for lost production. Selecting "No" the toll will calculate the losses reduction assiasated with a reduction in demand

## User Guide
WS1A Losses Tool Help guide
Tool Overview This tool has been developed to provide a calculation method for approximating the losses associated with flexible services to resolve network constraint. This tool utilises annual LLF data relating to average network losses across an entire DNO licence area. The tool is not anticipated to be used for detailed losses modelling; for a detailed losses report, an industry approved network modelling package should be used e.g. ISPA, Digsilent, Power factory, Windebut etc… The tool is only designed to operate using a single set of LLF values which cover both import and export losses.
Basic Functionality To start users must input information about the requirements for the service they are looking to procure. Users must select the license area, and the LLF period the service is being procured for. They should also enter the voltage level at which the service is required to alleviate constraints for E.g. a thermal overload at the primary transformer would trigger a requirement for a service to be provided to the "HV substation" voltage level. The requirement capacity should reflect the size of service required to alleviate the constraint in MWh. The requirement capacity sign Should reflect weather a service is required to increase demand or decrease demand e.g. for a demand overload of 200MWh through a transformer, a service would be procured to reduce demand. This service would be indicated in the calculator tool using a –ve sign (-200MWh) as shown in Figure 1. Once this information has been completed the tool will display a range of yellow boxes for the user to complete a summary of the flexible services they intend to procure split by type of service they will be providing and voltage that they service is connected via (Users should not fill in any information where a box has turned grey). For example a generator increasing output to provide a service to reduce overall network demand by 200MWh, connected to the LV network would be represented as shown in Figure 2. Provided that the user has matched the requirements and flexibility provided the tool well generate a calculated value for the estimated increase in losses. If there is an overall net reduction in losses this will be indicated by a negative value being displayed (highlighted in green text). If the user inputs incorrect information an error will display on screen. Additional functionality The tool provides additional functionality which will calculate additional losses associated with suppliers having to increase demand following a service delivery period. For example: a factory reduces production equating to a reduction in demand of 200 MWh; to make up for this loss of production the factory would increase demand by 200MWh during off peak hours. Note: the tool will always assume that the full capacity which has been reduced will be taken up during the period with the lowest LLF value. The tool also provides a feature which will calculate the losses associated with a electricity storage system/battery needing to recharge or discharge following a service delivery. If the storage system is going to be recharged utilising on site generation; this parameter should be set to "no”. The model does not take account of any inefficiently related data associated with recharging of the battery. Assumptions When a flexible service is procured the net result does not change the direction of energy flow at the voltage level it has being procured to resolve constraint at E.g. flexible service procured to resolve constraints at an HV substation Well not change the direction of flow of the EHV to HV transformer. When using a battery storage system; the recovery of energy will be recovered during the period with the lowest LLF factor. The tool does not account for any energy which is consumed within the network between the point of supply of flexible services and the constraint they have been procured to alleviate. The tool is only designed to operate using a single set of LLF values which cover both import and export losses. Additional Guidance note: Where it is know that the energy from a flexible service will be absorbed within the network prior to it reaching the point of constraint, the requirement voltage could be altered to make consideration of this. For example: If as a designer of the solution, you know that all the energy from a generator would be absorbed within a lower level of the network you could simulate this by lowering the voltage of the requirements within the tool. Likewise if you know that a proportion of the energy will be absorbed at the voltage level it is produced as you could carry out two calculations using the tool for the relevant proportions summing the two losses results together to get the end estimate. E.g. for a 500KWh constraint you may have a generator which half of its output is absorbed at LV and half which is absorbed within the HV network. So you would run the model twice. The first model would be run with 250KWh of requirement at LV being provided at LV. For the second model you would put 250KWh of requirement at HV and being provided from the LV network. |  | Figure 1
Figure 2

## SWEB - Annex 5 LLFs
These line loss factors have been audited by Elexon in accordance with BSCP128. The line loss factors that are approved by the BSC Panel consequently published on the Elexon website will take precedence and will be used in Settlement.
Western Power Distribution (South West) plc - LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Peak | Winter | Night | Other
Monday to Friday Mar to Oct |  |  | 00:00 - 06:30 23:30 - 24:00 | 06:30 - 23:30
Monday to Friday Nov to Feb | 16:00 - 19:00 | 06:30 - 16:00 | 00:00 - 06:30 23:30 - 24:00 | 19:00 - 23:30
Saturday and Sunday All Year |  |  | 00:00 - 06:30 23:30 - 24:00 | 06:30 - 23:30
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
132kV connected | 1.002 | 1.001 | 1.001 | 1.001
132/EHV connected | 1.005 | 1.005 | 1.006 | 1.006
132/HV connected | 1.006 | 1.005 | 1.006 | 1.006
EHV connected | 1.014 | 1.014 | 1.012 | 1.014 | 670, 671
High Voltage Substation | 1.02 | 1.019 | 1.018 | 1.02 | 522, 523, 525
High Voltage Network | 1.038 | 1.035 | 1.029 | 1.033 | 95, 96, 510, 521, 524
Low Voltage Substation | 1.052 | 1.051 | 1.052 | 1.051 | 93, 94, 526, 540, 551
Low Voltage Network | 1.067 | 1.063 | 1.062 | 1.062 | 10, 20, 30, 40, 91, 92, 110, 202, 203, 210, 251, 430, 527, 570, 581, 970, 977, 978, 979, 980
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Rolls Royce Filton HV Import | 1.02 | 1.019 | 1.018 | 1.02 | 198
Ashwater Auxiliary Import (LV) | 1.067 | 1.063 | 1.062 | 1.062 | 204
Otterham STOR Import | 1.005 | 1.005 | 1.006 | 1.006 | 250
Tregarrick Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 260
Freathy Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 261
Till House PV | 1.014 | 1.014 | 1.012 | 1.014 | 262
Outlands Wood PV | 1.014 | 1.014 | 1.012 | 1.014 | 263
Culmhead PV | 1.014 | 1.014 | 1.012 | 1.014 | 264
Whitchurch Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 265
Kingsland Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 266
Mendip Solar PV | 1.014 | 1.014 | 1.012 | 1.014 | 267
St Stephen PV | 1.014 | 1.014 | 1.012 | 1.014 | 268
Trewidland PV | 1.014 | 1.014 | 1.012 | 1.014 | 269
Watchfield Lawn PV | 1.014 | 1.014 | 1.012 | 1.014 | 270
Gover Park PV | 1.014 | 1.014 | 1.012 | 1.014 | 271
North Wayton PV | 1.014 | 1.014 | 1.012 | 1.014 | 272
Week Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 273
Cullompton PV | 1.014 | 1.014 | 1.012 | 1.014 | 274
Dinder Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 275
Kilmersdon Estate PV | 1.014 | 1.014 | 1.012 | 1.014 | 276
Pitts Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 277
Kerriers PV | 1.014 | 1.014 | 1.012 | 1.014 | 278
Ernesettle STOR | 1.014 | 1.014 | 1.012 | 1.014 | 279
Yew Tree Cottage PV | 1.014 | 1.014 | 1.012 | 1.014 | 280
Goonhilly PV | 1.014 | 1.014 | 1.012 | 1.014 | 281
Nanteague PV | 1.014 | 1.014 | 1.012 | 1.014 | 282
Bidwell Dartington PV | 1.014 | 1.014 | 1.012 | 1.014 | 283
New Row Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 284
Victoria (WBAR3) WF | 1.014 | 1.014 | 1.012 | 1.014 | 285
Four Barrows 2 PV | 1.014 | 1.014 | 1.012 | 1.014 | 286
Redlands Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 287
Tengore Lane PV | 1.014 | 1.014 | 1.012 | 1.014 | 288
Liverton Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 289
Yonder Parks PV | 1.014 | 1.014 | 1.012 | 1.014 | 290
Somerton Door PV | 1.014 | 1.014 | 1.012 | 1.014 | 291
Carditch Drove PV | 1.014 | 1.014 | 1.012 | 1.014 | 292
Capelands Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 293
East Youlstone WF | 1.014 | 1.014 | 1.012 | 1.014 | 294
Francis Court Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 295
Northwood PV | 1.014 | 1.014 | 1.012 | 1.014 | 296
Tricky Warren PV | 1.014 | 1.014 | 1.012 | 1.014 | 297
Iwood Lane PV | 1.014 | 1.014 | 1.012 | 1.014 | 298
Rydon Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 299
Balls Wood PV | 1.014 | 1.014 | 1.012 | 1.014 | 300
Ashlawn Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 301
Pencoose Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 302
Hawkers Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 303
Hurcott PV | 1.014 | 1.014 | 1.012 | 1.014 | 304
Garvinack Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 305
Newton Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 306
Coombeshead Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 307
Walland Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 308
Ashcombe PV | 1.014 | 1.014 | 1.012 | 1.014 | 309
Newnham Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 310
Roskrow Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 311
Parkview PV | 1.014 | 1.014 | 1.012 | 1.014 | 312
Towerhead Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 313
Rookery Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 314
Bystock Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 315
Pylle PVs Boundary Imports | 1.014 | 1.014 | 1.012 | 1.014 | 316
Burthy Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 317
Wilton Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 318
Coombe Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 319
Higher Bye Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 320
Wilton Farm WF | 1.014 | 1.014 | 1.012 | 1.014 | 321
Denzell Downs WF | 1.014 | 1.014 | 1.012 | 1.014 | 322
Puriton Landfill PV_1 | 1.014 | 1.014 | 1.012 | 1.014 | 323
Portworthy Dams PV Site 1 | 1.014 | 1.014 | 1.012 | 1.014 | 324
Wick Farm Boundary Imports | 1.014 | 1.014 | 1.012 | 1.014 | 325
Batsworthy Cross WF | 1.014 | 1.014 | 1.012 | 1.014 | 327
Portworthy Dams PV Site 2 | 1.014 | 1.014 | 1.012 | 1.014 | 328
Crewkerne PV Site 1 | 1.014 | 1.014 | 1.012 | 1.014 | 329
Crewkerne PV Site 2 | 1.014 | 1.014 | 1.012 | 1.014 | 330
Tonedale Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 331
Puriton Landfill PV_2 | 1.014 | 1.014 | 1.012 | 1.014 | 332
Red Hill Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 333
Chelwood PV | 1.014 | 1.014 | 1.012 | 1.014 | 334
West Carclaze Site 1 | 1.014 | 1.014 | 1.012 | 1.014 | 335
West Carclaze Site 2 | 1.014 | 1.014 | 1.012 | 1.014 | 336
Northmoor (embd) PV | 1.014 | 1.014 | 1.012 | 1.014 | 337
Nmoor Little Tinney WF | 1.014 | 1.014 | 1.012 | 1.014 | 338
Nmoor Little Balsdon WF | 1.014 | 1.014 | 1.012 | 1.014 | 339
Nmoor Hornacott PV | 1.014 | 1.014 | 1.012 | 1.014 | 340
Oakham Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 341
Carnemough Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 342
Ashwater WT Site 1 Import | 1.014 | 1.014 | 1.012 | 1.014 | 343
Makro Exeter STOR | 1.014 | 1.014 | 1.012 | 1.014 | 344
Great Hounbeare PV | 1.014 | 1.014 | 1.012 | 1.014 | 345
Withy Drove PV | 1.014 | 1.014 | 1.012 | 1.014 | 346
Water Lane STOR | 1.014 | 1.014 | 1.012 | 1.014 | 347
Montys Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 348
Lawrence Weston PV | 1.014 | 1.014 | 1.012 | 1.014 | 349
Dunsland Cross WF | 1.014 | 1.014 | 1.012 | 1.014 | 350
Trerule Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 351
Nancrossa Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 352
Wick Farm West | 1.014 | 1.014 | 1.012 | 1.014 | 353
LWestPNtWk SevernCom PV | 1.014 | 1.014 | 1.012 | 1.014 | 354
LWestPNtWk Site 2 PV | 1.014 | 1.014 | 1.012 | 1.014 | 355
Tamerton Bridge STOR | 1.014 | 1.014 | 1.012 | 1.014 | 356
Ashwater PV Site 2 Import | 1.014 | 1.014 | 1.012 | 1.014 | 357
Bodwen PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 358
Sharland Farm PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 359
Stoneshill PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 360
Nmoor Parsonage Wood PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 361
Axe View PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 362
Place Barton PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 363
Old Stone farm PV Import | 1.014 | 1.014 | 1.012 | 1.014 | 364
Cattedown STOR Import | 1.014 | 1.014 | 1.012 | 1.014 | 365
Barton Hill Way STOR Import | 1.014 | 1.014 | 1.012 | 1.014 | 366
Lockleaze Battery Import | 1.014 | 1.014 | 1.012 | 1.014 | 367
Imerys Blackpool | 1.02 | 1.019 | 1.018 | 1.02 | 600
Otterham WT Feeder1 | 1.005 | 1.005 | 1.006 | 1.006 | 603
Otterham WT Feeder2 | 1.005 | 1.005 | 1.006 | 1.006 | 604
Wyld Meadow PV Farm | 1.014 | 1.014 | 1.012 | 1.014 | 607
Prince Rock STOR | 1.014 | 1.014 | 1.012 | 1.014 | 608
Fulford Solar | 1.014 | 1.014 | 1.012 | 1.014 | 609
Bradon Farm | 1.014 | 1.053 | 1.052 | 1.053 | 612
Carland Cross | 1.014 | 1.014 | 1.012 | 1.014 | 613
Cold Northcott | 1.014 | 1.014 | 1.012 | 1.014 | 614
Forest Moor Wind 1 | 1.014 | 1.014 | 1.012 | 1.014 | 615
Forest Moor Wind 2 | 1.014 | 1.014 | 1.012 | 1.014 | 616
Four Burrows | 1.014 | 1.014 | 1.012 | 1.014 | 617
Canworthy PV | 1.002 | 1.001 | 1.007 | 1.001 | 618
St. Breock | 1.014 | 1.014 | 1.012 | 1.014 | 619
Babcock Marine Central Intake | 1.014 | 1.014 | 1.014 | 1.014 | 620
W4B Generation Seabank | 1.014 | 1.014 | 1.012 | 1.014 | 622
Denbrook Wind Farm | 1.014 | 1.014 | 1.012 | 1.014 | 623
Wavehub Hayle | 1.014 | 1.014 | 1.012 | 1.014 | 624
Marsh Barton | 1.011 | 1.011 | 1.011 | 1.011 | 625
Connon Bridge Landfill | 1.014 | 1.014 | 1.012 | 1.014 | 626
Chelson Generator | 1.014 | 1.014 | 1.012 | 1.014 | 627
Darracott | 1.014 | 1.014 | 1.012 | 1.014 | 628
Bears Down | 1.014 | 1.014 | 1.012 | 1.014 | 629
Untd Mns Redruth St.Day | 1.014 | 1.014 | 1.012 | 1.014 | 632
Shooter's Bottom | 1.014 | 1.014 | 1.012 | 1.014 | 633
Heathfield | 1.014 | 1.014 | 1.012 | 1.014 | 634
Goonhilly | 1.014 | 1.014 | 1.012 | 1.014 | 635
Delabole | 1.014 | 1.014 | 1.012 | 1.014 | 636
Fullabrook | 1.002 | 1.001 | 1.009 | 1.001 | 637
Hemerdon Mine | 1.026 | 1.026 | 1.025 | 1.025 | 638
Trenoweth Farm | 1.014 | 1.014 | 1.012 | 1.014 | 639
Rolls Royce Filton TT | 1.014 | 1.014 | 1.012 | 1.014 | 640
Woodland Barton Farm | 1.014 | 1.014 | 1.012 | 1.014 | 642
Manor Farm | 1.014 | 1.014 | 1.012 | 1.014 | 643
Churchtown Farm | 1.014 | 1.014 | 1.012 | 1.014 | 644
Trenouth Farm | 1.014 | 1.014 | 1.012 | 1.014 | 645
West Kingsmill | 1.014 | 1.014 | 1.012 | 1.014 | 646
Howton Farm | 1.014 | 1.014 | 1.012 | 1.014 | 647
Chynoweth Farm | 1.014 | 1.014 | 1.012 | 1.014 | 648
Newton Downs Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 649
ROF Puriton | 1.014 | 1.014 | 1.012 | 1.014 | 650
East Langford | 1.014 | 1.014 | 1.012 | 1.014 | 652
Ninnis Farm | 1.014 | 1.014 | 1.012 | 1.014 | 653
Willsland | 1.014 | 1.014 | 1.012 | 1.014 | 654
Eastcombe Farm | 1.014 | 1.014 | 1.012 | 1.014 | 655
Bratton Flemming | 1.014 | 1.014 | 1.012 | 1.014 | 656
Beaford Brook | 1.014 | 1.014 | 1.012 | 1.014 | 657
Park Wall | 1.014 | 1.014 | 1.012 | 1.014 | 658
Bradford | 1.014 | 1.014 | 1.012 | 1.014 | 659
Causilgey | 1.014 | 1.014 | 1.012 | 1.014 | 662
Beechgrove | 1.014 | 1.014 | 1.012 | 1.014 | 663
Isles of Scilly EHV | 1.02 | 1.019 | 1.018 | 1.02 | 664
Blackditch | 1.014 | 1.014 | 1.012 | 1.014 | 665
Helius Biomass | 1.002 | 1.001 | 1.001 | 1.001 | 667
Bristol Port Co Avonmouth Dock | 1.02 | 1.019 | 1.018 | 1.02 | 669
Northmoor PV | 1.002 | 1.001 | 1.001 | 1.001 | 672
CERC St Dennis | 1.002 | 1.001 | 1.001 | 1.001 | 673
Severnside ERC | 1.002 | 1.001 | 1.001 | 1.001 | 674
Alveston WF Import | 1.002 | 1.001 | 1.001 | 1.001 | 675
Nexfor Ltd (Caberboard) | 1.041 | 1.041 | 1.039 | 1.039 | 690
SWW Tamar | 1.059 | 1.059 | 1.059 | 1.06 | 692
SWW Roadford | 1.037 | 1.037 | 1.037 | 1.037 | 694
St. Regis, Watchet | 1.01 | 1.01 | 1.01 | 1.01 | 695
Tarmac Stancombe Quarry | 1.036 | 1.037 | 1.036 | 1.036 | 696
MOD Abbeywood | 1.02 | 1.019 | 1.018 | 1.02 | 697
Hewlett Packard | 1.02 | 1.019 | 1.018 | 1.02 | 698
Bristol Water Blagdon Pump Stn | 1.02 | 1.019 | 1.018 | 1.02 | 699
Bristol International Airport | 1.02 | 1.019 | 1.018 | 1.02 | 700
British Gas Hallen | 1.02 | 1.019 | 1.018 | 1.02 | 701
Bristol Port Co R.Portbury Doc | 1.02 | 1.019 | 1.018 | 1.02 | 702
Whatley Quarry | 1.02 | 1.019 | 1.018 | 1.02 | 703
Falmouth Docks | 1.02 | 1.019 | 1.018 | 1.02 | 704
Astra Zeneca Hallen | 1.02 | 1.019 | 1.018 | 1.02 | 705
Dairy Crest Davidstow | 1.02 | 1.019 | 1.018 | 1.02 | 706
Broadpath Landfill | 1.02 | 1.019 | 1.018 | 1.02 | 707
Imerys Torycombe | 1.02 | 1.019 | 1.018 | 1.02 | 708
RUH | 1.02 | 1.019 | 1.018 | 1.02 | 709
Hill Barton Business Park | 1.02 | 1.019 | 1.018 | 1.02 | 712
Avonmouth BCC Wind Farm | 1.014 | 1.014 | 1.012 | 1.014 | 713
Bodiniel PV Park | 1.014 | 1.014 | 1.012 | 1.014 | 714
Garlenick Wind Farm | 1.014 | 1.014 | 1.012 | 1.014 | 715
Warleigh Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 716
Winnard's Perch PV | 1.014 | 1.014 | 1.012 | 1.014 | 717
Galsworthy WF | 1.002 | 1.001 | 1.001 | 1.001 | 718
Otterham WF | 1.002 | 1.001 | 1.001 | 1.001 | 719
BAe Filton | 1.02 | 1.019 | 1.018 | 1.02 | 720
Bristol Energy | 1.002 | 1.002 | 1.002 | 1.002 | 750
LANGAGE | 1.014 | 1.014 | 1.012 | 1.014 | 759
Imerys Drinnick | 1.02 | 1.019 | 1.018 | 1.02 | 797
Imerys Bugle | 1.02 | 1.019 | 1.018 | 1.02 | 798
Imerys Trebal | 1.02 | 1.019 | 1.018 | 1.02 | 799
Imerys Par Harbour | 1.02 | 1.019 | 1.018 | 1.02 | 800
Babcock Marine North Intake | 1.013 | 1.013 | 1.012 | 1.012 | 805
Marley Thatch PV | 1.014 | 1.014 | 1.012 | 1.014 | 810
Bristol Royal Infirmary | 1.02 | 1.019 | 1.018 | 1.02 | 811
Bristol University 33/11kV | 1.02 | 1.019 | 1.018 | 1.02 | 812
Burrowton Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 815
Callington Solar | 1.014 | 1.014 | 1.012 | 1.014 | 816
Hope Solar | 1.014 | 1.014 | 1.012 | 1.014 | 817
Avonmouth Biogas | 1.009 | 1.009 | 1.009 | 1.009 | 818
Nether Mill Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 819
Slade Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 820
Rew Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 821
Higher Trenhayle PV | 1.014 | 1.014 | 1.012 | 1.014 | 822
Middle Treworder PV | 1.014 | 1.014 | 1.012 | 1.014 | 823
Penhale Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 824
Ayshford Court PV | 1.014 | 1.014 | 1.012 | 1.014 | 825
West Hill PV | 1.014 | 1.014 | 1.012 | 1.014 | 826
Knockworthy Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 827
University of Bath | 1.012 | 1.012 | 1.011 | 1.011 | 828
Trekenning Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 829
Four Burrows PV | 1.014 | 1.014 | 1.012 | 1.014 | 830
Glebe Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 831
Hurlingpot PV | 1.014 | 1.014 | 1.012 | 1.014 | 832
Halse Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 833
Hatchlands Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 834
Higher Trevartha PV | 1.014 | 1.014 | 1.012 | 1.014 | 835
High Down WF | 1.014 | 1.014 | 1.012 | 1.014 | 836
Ford Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 837
Lower Tinacre PV | 1.014 | 1.014 | 1.012 | 1.014 | 838
Trequite Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 839
Yonder Netherton PV | 1.014 | 1.014 | 1.012 | 1.014 | 840
Higher Tregarne PV | 1.014 | 1.014 | 1.012 | 1.014 | 841
Higher North Beer PV | 1.014 | 1.014 | 1.012 | 1.014 | 842
Horsacott Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 843
Langunnett Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 844
Trefinnick Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 845
Little Trevease PV | 1.014 | 1.014 | 1.012 | 1.014 | 846
Marksbury PV | 1.014 | 1.014 | 1.012 | 1.014 | 847
Cobbs Cross PV | 1.014 | 1.014 | 1.012 | 1.014 | 848
Newlands Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 849
Cricket St Thomas PV | 1.014 | 1.014 | 1.012 | 1.014 | 850
Parsonage Barn PV | 1.014 | 1.014 | 1.012 | 1.014 | 851
Hewas PV Farm | 1.014 | 1.014 | 1.012 | 1.014 | 852
Crinacott Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 853
Penare Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 854
Aller Court PV | 1.014 | 1.014 | 1.012 | 1.014 | 855
Webbery Barton WF | 1.014 | 1.014 | 1.012 | 1.014 | 856
Stonebarrow Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 857
Whitley Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 858
New Rendy Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 859
Tregassow Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 860
Pitworthy PV | 1.014 | 1.014 | 1.012 | 1.014 | 861
Foxcombe PV | 1.014 | 1.014 | 1.012 | 1.014 | 862
Rexon Cross PV | 1.014 | 1.014 | 1.012 | 1.014 | 863
Hazard Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 864
Luscott Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 865
Grange Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 866
Derriton Fields PV | 1.014 | 1.014 | 1.012 | 1.014 | 867
Cleave Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 868
Woolavington PV | 1.014 | 1.014 | 1.012 | 1.014 | 869
Trehawke Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 870
H Berechapel Biogas | 1.014 | 1.014 | 1.012 | 1.014 | 871
Bommertown PV | 1.014 | 1.014 | 1.012 | 1.014 | 872
Carloggas Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 873
Hexworthy Barton PV | 1.014 | 1.014 | 1.012 | 1.014 | 874
Chalhanger Farm PV | 1.014 | 1.014 | 1.012 | 1.014 | 875
Viridor Chittening EFW Import | 1.014 | 1.014 | 1.012 | 1.014 | 876
Alders Way STOR Import | 1.014 | 1.014 | 1.012 | 1.014 | 877
Rockingham South Imports | 1.014 | 1.014 | 1.012 | 1.014 | 878
Simms (AVMO7J imports) | 1.038 | 1.035 | 1.029 | 1.033 | 961
Flour Mills (AVMO7J imports) | 1.038 | 1.035 | 1.029 | 1.033 | 962
726: Indian Queens Standby Supply | 1.067 | 1.063 | 1.062 | 1.062 | 7049
763:Seabank Standby Supply | 1.038 | 1.035 | 1.029 | 1.033 | 7118
763:Seabank Standby Supply | 1.038 | 1.035 | 1.029 | 1.033 | 7122
Bridgwater District Energy | 1.009 | 1.01 | 1.012 | 1.01 | 7158
HammerlyDown | 1.005 | 1.005 | 1.006 | 1.006 | 7293
The Drove Imports | 1.038 | 1.035 | 1.029 | 1.033 | 7307
Water Lane Imports | 1.014 | 1.014 | 1.012 | 1.014 | 7319
Plymouth Rock Imports | 1.014 | 1.014 | 1.012 | 1.014 | 7341
Barton Hill Imports | 1.014 | 1.014 | 1.012 | 1.014 | 7317
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Tregarrick Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 371
Freathy Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 372
Till House PV Export | 1.014 | 0.998 | 1.012 | 0.998 | 373
Outlands Wood PV Export | 1.014 | 1.029 | 1.012 | 1.029 | 374
Culmhead PV Export | 1.014 | 1.014 | 1.012 | 1.013 | 375
Whitchurch Farm PV Export | 1.014 | 1.036 | 1.012 | 1.036 | 376
Kingsland Barton PV Export | 1.014 | 1.046 | 1.012 | 1.046 | 377
Mendip Solar PV Export | 1.014 | 1.041 | 1.012 | 1.04 | 378
St Stephen PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 379
Trewidland PV Export | 1.014 | 1.022 | 1.012 | 1.022 | 380
Watchfield Lawn PV Export | 1.014 | 1.071 | 1.012 | 1.069 | 381
Gover Park PV Export | 1.014 | 1.033 | 1.012 | 1.031 | 382
North Wayton PV Export | 1.014 | 1.008 | 1.012 | 1.008 | 383
Week Farm PV Export | 1.014 | 1.043 | 1.012 | 1.042 | 384
Cullompton PV Export | 1.014 | 1.039 | 1.012 | 1.039 | 385
Dinder Farm PV Export | 1.014 | 1.061 | 1.012 | 1.061 | 386
Rolls Royce Filton Export | 1.014 | 1.014 | 1.012 | 1.014 | 387
Pitts Farm PV Export | 1.014 | 1.061 | 1.012 | 1.061 | 388
Kerriers PV Export | 1.014 | 1.028 | 1.012 | 1.027 | 389
Ernesettle STOR Export | 1.009 | 1.014 | 1.012 | 1.014 | 390
Yew Tree Cottage PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 391
Goonhilly PV Export | 1.014 | 1.075 | 1.012 | 1.074 | 392
Nanteague PV Export | 1.014 | 1.014 | 1.012 | 1.013 | 393
Bidwell Dartington PV Export | 1.014 | 1.007 | 1.012 | 1.007 | 394
New Row Farm PV Export | 1.014 | 1.069 | 1.012 | 1.069 | 395
Victoria (WBAR3) WF Export | 1.017 | 1.016 | 1.017 | 1.017 | 396
Four Burrows 2 PV Export | 1.014 | 1.02 | 1.012 | 1.019 | 397
Redlands Farm PV Export | 1.014 | 1.014 | 1.012 | 1.013 | 398
Tengore Lane PV Export | 1.014 | 1.058 | 1.012 | 1.057 | 399
Liverton Farm PV Export | 1.014 | 1.017 | 1.012 | 1.017 | 400
Yonder Parks PV Export | 1.014 | 1.04 | 1.012 | 1.04 | 401
Somerton Door PV Export | 1.014 | 1.046 | 1.012 | 1.045 | 402
Carditch Drove PV Export | 1.014 | 1.019 | 1.012 | 1.019 | 403
Capelands Farm PV Export | 1.014 | 1.046 | 1.012 | 1.043 | 404
East Youlstone WF Export | 1.034 | 1.035 | 1.037 | 1.038 | 405
Francis Court Farm PV Export | 1.014 | 1.01 | 1.012 | 1.009 | 406
Northwood PV Export | 1.014 | 1.013 | 1.012 | 1.012 | 407
Tricky Warren PV Export | 1.014 | 1.015 | 1.012 | 1.014 | 408
Iwood Lane PV Export | 1.014 | 1.017 | 1.012 | 1.016 | 409
Rydon Farm PV Export | 1.014 | 1.02 | 1.012 | 1.019 | 410
Balls Wood PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 411
Ashlawn Farm PV Export | 1.014 | 1.038 | 1.012 | 1.036 | 412
Pencoose Farm PV Export | 1.014 | 1.031 | 1.012 | 1.031 | 413
Hawkers Farm PV Export | 1.014 | 1.032 | 1.012 | 1.029 | 414
Hurcott PV Export | 1.014 | 1.036 | 1.012 | 1.035 | 415
Garvinack Farm PV Export | 1.014 | 1.018 | 1.012 | 1.017 | 416
Newton Barton PV Export | 1.014 | 1.007 | 1.012 | 1.005 | 417
Coombeshead Farm PV Export | 1.014 | 1.026 | 1.012 | 1.025 | 418
Walland Farm PV Export | 1.014 | 1.045 | 1.012 | 1.043 | 419
Ashcombe PV Export | 1.014 | 1.043 | 1.012 | 1.042 | 420
Newnham Farm PV Export | 1.014 | 1.017 | 1.012 | 1.016 | 421
Roskrow Barton PV Export | 1.014 | 1.04 | 1.012 | 1.039 | 422
Parkview PV Export | 1.014 | 1.025 | 1.012 | 1.024 | 423
Towerhead Farm PV Export | 1.014 | 1.019 | 1.012 | 1.018 | 424
Rookery Farm PV Export | 1.014 | 1.018 | 1.012 | 1.018 | 425
Bystock Farm PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 426
Pylle PV Site 1 Export | 1.014 | 1.066 | 1.012 | 1.065 | 427
Burthy Farm PV Export | 1.014 | 1.017 | 1.018 | 1.017 | 428
Wilton Farm PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 429
Coombe Farm PV Export | 1.014 | 1.017 | 1.012 | 1.016 | 431
Higher Bye Farm PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 432
Wilton Farm WF Export | 1.013 | 1.013 | 1.013 | 1.013 | 433
Denzell Down WF Export | 1.02 | 1.02 | 1.021 | 1.021 | 434
Puriton Landfill PV_1 Export | 1.014 | 1.032 | 1.012 | 1.031 | 435
PortworthyDams PV Site1 Export | 1.014 | 1.03 | 1.012 | 1.029 | 436
Wick Farm Site 1 PV Export | 1.014 | 1.032 | 1.012 | 1.032 | 437
Wick Farm Site 2 PV Export | 1.014 | 1.032 | 1.012 | 1.032 | 438
Batsworthy Cross WF Export | 1.033 | 1.032 | 1.039 | 1.039 | 439
PortworthyDams PV Site2 Export | 1.014 | 1.03 | 1.012 | 1.029 | 440
Crewkerne PV Site 1 Export | 1.014 | 1.06 | 1.012 | 1.06 | 441
Crewkerne PV Site 2 Export | 1.014 | 1.06 | 1.012 | 1.06 | 442
Tonedale Farm PV Export | 1.014 | 1.019 | 1.012 | 1.019 | 443
Puriton Landfill PV_2 Export | 1.014 | 1.032 | 1.012 | 1.031 | 444
Pylle PV Site 2 Export | 1.014 | 1.066 | 1.012 | 1.065 | 445
Chelwood PV Export | 1.014 | 1.031 | 1.012 | 1.032 | 446
Red Hill Farm PV Export | 1.014 | 1.019 | 1.012 | 1.018 | 447
West Carclaze Site 1 Export | 1.014 | 1.014 | 1.012 | 1.014 | 448
West Carclaze Site 2 Export | 1.014 | 1.014 | 1.012 | 1.014 | 449
Northmoor (embd) PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 450
Nmoor Little Tinney WF Export | 1.014 | 1.014 | 1.012 | 1.014 | 451
Nmoor Little Balsdon WF Export | 1.014 | 1.014 | 1.012 | 1.014 | 452
Nmoor Hornacott PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 453
Oakham Farm PV Export | 1.014 | 1.004 | 1.012 | 1.004 | 454
Carnemough Farm PV Export | 1.014 | 1.019 | 1.012 | 1.018 | 455
Ashwater WT Site 1 Export | 1.03 | 1.029 | 1.03 | 1.029 | 456
Makro Exeter STOR Export | 1.018 | 1.02 | 1.012 | 1.02 | 457
Great Hounbeare PV Export | 1.014 | 1.03 | 1.012 | 1.029 | 458
Withy Drove PV Export | 1.014 | 1.022 | 1.012 | 1.022 | 459
Water Lane STOR Export | 1.014 | 1.014 | 1.012 | 1.014 | 460
Montys Farm PV Export | 1.014 | 1.008 | 1.012 | 1.008 | 461
Lawrence Weston PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 462
Dunsland Cross WF Export | 1.034 | 1.034 | 1.035 | 1.035 | 463
Trerule Farm PV Export | 1.014 | 1.015 | 1.012 | 1.015 | 464
Nancrossa Farm PV Export | 1.014 | 1.024 | 1.012 | 1.024 | 465
Wick Farm West Export | 1.014 | 1.032 | 1.012 | 1.031 | 466
LWestPNtWk SevernCom PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 467
LWestPNtWk Site 2 PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 468
Tamerton Bridge STOR Export | 1.006 | 1.014 | 1.012 | 1.014 | 469
Ashwater PV Site 2 Export | 1.03 | 1.029 | 1.03 | 1.029 | 470
Bodwen PV Export | 1.014 | 1.017 | 1.012 | 1.017 | 471
Sharland Farm PV Export | 1.014 | 1.105 | 1.012 | 1.104 | 472
Stoneshill PV Export | 1.014 | 1.025 | 1.012 | 1.024 | 473
Nmoor Parsonage Wood PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 474
Axe View PV Export | 1.014 | 1.019 | 1.012 | 1.019 | 475
Place Barton PV Export | 1.014 | 1.03 | 1.012 | 1.03 | 476
Old Stone Farm PV Export | 1.014 | 1.042 | 1.012 | 1.041 | 477
Cattedown STOR Export | 1.014 | 1.014 | 1.012 | 1.014 | 478
Barton Hill Way STOR Export | 1.014 | 1.014 | 1.012 | 1.014 | 479
Lockleaze Battery Export | 1.014 | 1.014 | 1.012 | 1.014 | 480
Viridor Chittening EFW Export | 1.014 | 1.014 | 1.012 | 1.014 | 481
Alders Way STOR Export | 1.014 | 1.014 | 1.012 | 1.014 | 482
Rockingham South Exports | 1.014 | 1.014 | 1.012 | 1.014 | 483
Otterham STOR Export | 1.005 | 1.005 | 1.006 | 1.006 | 529
Northmoor PV Export | 1.002 | 1.001 | 1.001 | 1.001 | 585
CERC St Dennis Export | 1 | 1 | 1 | 1 | 586
Severnside ERC Export | 1 | 1 | 1 | 1 | 587
Alveston WF Export | 1.002 | 1.001 | 1.001 | 1.001 | 588
Imerys Blackpool Export | 1.02 | 1.019 | 1.018 | 1.02 | 601
Blackditch Export | 1.014 | 1.044 | 1.012 | 1.044 | 666
Helius Biomass Export | 1.002 | 1.001 | 1.001 | 1.001 | 668
SWW Roadford Export | 1.014 | 1.014 | 1.012 | 1.014 | 693
RUH Export | 1.02 | 1.019 | 1.018 | 1.02 | 722
Babcock Marine Central Export | 1.021 | 1.021 | 1.02 | 1.02 | 723
Trenoweth Farm Export | 1.014 | 1.015 | 1.012 | 1.014 | 724
Woodland Barton Farm Export | 1.014 | 1.016 | 1.012 | 1.016 | 725
Manor Farm Export | 1.014 | 1.012 | 1.012 | 1.012 | 726
Churchtown Farm Export | 1.014 | 1.037 | 1.012 | 1.037 | 727
Trenouth Farm Export | 1.014 | 1.049 | 1.012 | 1.049 | 728
West Kingsmill Export | 1.014 | 1.014 | 1.012 | 1.014 | 729
Howton Farm Export | 1.014 | 1.025 | 1.012 | 1.025 | 732
Babcock Marine North Export | 1.014 | 1.014 | 1.021 | 1.021 | 733
Newton Downs Farm PV Export | 1.014 | 1.021 | 1.012 | 1.021 | 734
East Langford Export | 1.014 | 1.055 | 1.012 | 1.055 | 735
Ninnis Farm Export | 1.014 | 1.012 | 1.012 | 1.012 | 736
Willsland Export | 1.014 | 1.051 | 1.012 | 1.051 | 737
Eastcombe Farm Export | 1.014 | 1.03 | 1.012 | 1.029 | 738
Bratton Flemming Export | 1.014 | 1.048 | 1.012 | 1.046 | 739
Beaford Brook Export | 1.014 | 1.105 | 1.012 | 1.104 | 740
Exeter Power Export | 1.01 | 1.011 | 1.001 | 1.011 | 741
Park Wall Export | 1.014 | 1.007 | 1.012 | 1.007 | 742
Bradford Export | 1.014 | 1.025 | 1.012 | 1.024 | 743
Causilgey Export | 1.014 | 1.028 | 1.012 | 1.028 | 744
Beechgrove Export | 1.014 | 1.01 | 1.012 | 1.01 | 745
Hill Barton Bus Park Export | 1.02 | 1.019 | 1.018 | 1.02 | 746
Wavehub Hayle Export | 1.014 | 1.014 | 1.012 | 1.014 | 747
Denbrook Wind Farm Export | 1.007 | 1.006 | 1.007 | 1.007 | 748
W4B Generation Seabank Export | 1.014 | 1.014 | 1.012 | 1.014 | 749
Bristol Energy Export | 1.002 | 1.002 | 1.001 | 1.003 | 751
Connon Bridge Landfill export | 1.038 | 1.038 | 1.039 | 1.039 | 752
Chelson Generator Export | 1.014 | 1.014 | 1.012 | 1.014 | 753
Darracott Export | 1.072 | 1.072 | 1.073 | 1.073 | 754
Untd Mns Redruth St.Day Export | 1.035 | 1.035 | 1.035 | 1.035 | 757
Shooter's Bottom Export | 1.04 | 1.04 | 1.04 | 1.04 | 758
Heathfield Export | 1.037 | 1.037 | 1.037 | 1.037 | 760
Goonhilly Export | 1.058 | 1.058 | 1.064 | 1.065 | 761
Delabole EHV Export | 1.044 | 1.044 | 1.047 | 1.047 | 762
Fullabrook EHV Export | 1.005 | 1.005 | 1.006 | 1.007 | 763
Bear's Down Export | 1.037 | 1.038 | 1.04 | 1.04 | 764
Bradon Farm Export | 1.036 | 1.048 | 1.012 | 1.051 | 765
Carland Cross Export | 1.024 | 1.024 | 1.027 | 1.027 | 766
Cold Northcott Export | 1.065 | 1.064 | 1.068 | 1.068 | 767
Forest Moor Wind 1 Export | 1.06 | 1.06 | 1.061 | 1.061 | 768
Forest Moor Wind 2 Export | 1.061 | 1.061 | 1.062 | 1.062 | 769
Four Burrows Export | 1.036 | 1.036 | 1.037 | 1.037 | 770
Isles of Scilly EHV Export | 1.02 | 1.019 | 1.018 | 1.02 | 772
St Breock Export | 1.024 | 1.024 | 1.028 | 1.03 | 775
Avonmouth BCC Wind Farm Export | 1.002 | 1.002 | 1.002 | 1.002 | 776
Bodiniel PV Park Export | 1.014 | 1.029 | 1.012 | 1.029 | 777
Garlenick Wind Farm Export | 1.007 | 1.007 | 1.008 | 1.008 | 778
Warleigh Barton PV Export | 1.014 | 1.012 | 1.012 | 1.012 | 779
Winnard's Perch PV Export | 1.014 | 1.041 | 1.012 | 1.041 | 780
Galsworthy WF Export | 1.009 | 1.009 | 1.009 | 1.009 | 781
Otterham WF Export | 1.002 | 1.001 | 1.001 | 1.001 | 782
Canworthy PV Export | 1.007 | 1.006 | 1.001 | 1.006 | 783
Otterham WT Feeder1 Export | 1.005 | 1.005 | 1.006 | 1.006 | 785
Otterham WT Feeder2 Export | 1.005 | 1.005 | 1.006 | 1.006 | 786
Wyld Meadow PV Farm Export | 1.014 | 1.01 | 1.012 | 1.01 | 789
Marley Thatch PV Export | 1.014 | 1.022 | 1.012 | 1.022 | 790
Prince Rock STOR Export | 1.015 | 1.014 | 1.012 | 1.014 | 791
Burrowton Farm PV Export | 1.014 | 0.998 | 1.012 | 0.998 | 792
Bristol Royal Infirmary Export | 1.02 | 1.019 | 1.018 | 1.02 | 793
Imerys Torycombe export | 1.02 | 1.019 | 1.018 | 1.02 | 794
Whatley Quarry Export | 1.02 | 1.019 | 1.018 | 1.02 | 795
Imerys Trebal Export | 1.02 | 1.019 | 1.018 | 1.02 | 801
Imerys Par Harbour Export | 1.02 | 1.019 | 1.018 | 1.02 | 802
Imerys Bugle Export | 1.02 | 1.019 | 1.018 | 1.02 | 803
Imerys Drinnick Export | 1.02 | 1.019 | 1.018 | 1.02 | 804
Avonmouth Docks Export | 1.02 | 1.019 | 1.018 | 1.02 | 806
Portbury Dock Export | 1.02 | 1.019 | 1.018 | 1.02 | 807
BGAS Hallen Exports | 1.02 | 1.019 | 1.018 | 1.02 | 808
Broadpath Landfill Exports | 1.02 | 1.019 | 1.018 | 1.02 | 809
Callington Solar Export | 1.014 | 1.058 | 1.012 | 1.057 | 900
Hope Solar Export | 1.014 | 1.038 | 1.012 | 1.037 | 901
Fulford Solar Export | 1.014 | 1.014 | 1.012 | 1.014 | 902
Avonmouth Biogas Export | 1.008 | 1.008 | 1.008 | 1.008 | 903
Nether Mill Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 904
Slade Farm PV Export | 1.014 | 1.048 | 1.012 | 1.048 | 905
Rew Farm PV Export | 1.014 | 1.03 | 1.012 | 1.03 | 906
Higher Trenhayle PV Export | 1.014 | 1.061 | 1.012 | 1.061 | 907
Middle Treworder PV Export | 1.014 | 1.037 | 1.012 | 1.037 | 908
Penhale Farm PV Export | 1.014 | 1.04 | 1.012 | 1.039 | 909
Ayshford Court PV Export | 1.014 | 1.037 | 1.012 | 1.037 | 910
West Hill PV Export | 1.014 | 1.039 | 1.012 | 1.037 | 911
Knockworthy Farm PV Export | 1.014 | 1.065 | 1.012 | 1.065 | 912
Trekenning Farm PV Export | 1.014 | 1.01 | 1.012 | 1.009 | 914
Four Burrows PV Export | 1.014 | 1.042 | 1.012 | 1.041 | 915
Glebe Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 916
Hurlingpot PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 917
Halse Farm PV Export | 1.014 | 1.01 | 1.012 | 1.01 | 918
Hatchlands Farm PV Export | 1.014 | 1.016 | 1.012 | 1.016 | 919
Higher Trevartha PV Export | 1.014 | 1.038 | 1.012 | 1.038 | 920
High Down WF Export | 1.014 | 1.014 | 1.012 | 1.014 | 921
Ford Farm PV Export | 1.014 | 1.045 | 1.012 | 1.044 | 922
Lower Tinacre PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 923
Trequite Farm PV Export | 1.014 | 1.017 | 1.012 | 1.017 | 924
Yonder Netherton PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 925
Higher Tregarne PV Export | 1.014 | 1.037 | 1.012 | 1.036 | 926
Higher North Beer PV Export | 1.014 | 1.08 | 1.012 | 1.079 | 927
Horsacott Farm PV Export | 1.014 | 1.026 | 1.012 | 1.026 | 928
Langunnett Farm PV Export | 1.014 | 1.041 | 1.012 | 1.039 | 929
Trefinnick Farm PV Export | 1.014 | 1.063 | 1.012 | 1.063 | 930
Little Trevease PV Export | 1.014 | 1.025 | 1.012 | 1.025 | 931
Marksbury PV Export | 1.014 | 1.042 | 1.012 | 1.041 | 932
Cobbs Cross PV Export | 1.014 | 1.018 | 1.012 | 1.018 | 933
Newlands Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 934
Cricket St Thomas PV Export | 1.014 | 1.035 | 1.012 | 1.035 | 935
Parsonage Barn PV Export | 1.014 | 1.038 | 1.012 | 1.037 | 936
Hewas PV Farm Export | 1.014 | 1.008 | 1.012 | 1.008 | 937
Crinacott Farm PV Export | 1.014 | 1.025 | 1.012 | 1.025 | 938
Penare Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 939
Aller Court PV Export | 1.014 | 1.03 | 1.012 | 1.03 | 940
Webbery Barton WF Export | 1.014 | 1.014 | 1.012 | 1.014 | 941
Stonebarrow Farm PV Export | 1.014 | 1.01 | 1.012 | 1.01 | 942
Whitley Farm PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 943
New Rendy Farm PV Export | 1.014 | 1.011 | 1.012 | 1.01 | 944
Tregassow Farm PV Export | 1.014 | 1.024 | 1.012 | 1.023 | 945
Pitworthy PV Export | 1.014 | 1.023 | 1.012 | 1.023 | 946
Foxcombe PV Export | 1.014 | 1.036 | 1.012 | 1.036 | 947
Rexon Cross PV Export | 1.014 | 1.039 | 1.012 | 1.038 | 948
Hazard Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 949
Luscott Barton PV Export | 1.014 | 1.039 | 1.012 | 1.038 | 950
Grange Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 951
Derriton Fields PV Export | 1.014 | 1.024 | 1.012 | 1.023 | 952
Cleave Farm PV Export | 1.014 | 1.043 | 1.012 | 1.042 | 953
Woolavington PV Export | 1.014 | 1.022 | 1.012 | 1.021 | 954
Trehawke Farm PV Export | 1.014 | 1.013 | 1.012 | 1.013 | 955
H Berechapel Biogas Export | 1.041 | 1.041 | 1.041 | 1.041 | 956
Bommertown PV Export | 1.014 | 1.059 | 1.012 | 1.056 | 957
Carloggas Farm PV Export | 1.014 | 1.018 | 1.012 | 1.018 | 958
Hexworthy Barton PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 959
Chalhanger Farm PV Export | 1.014 | 1.014 | 1.012 | 1.014 | 960
Rolls Royce Filton HV Export | 1.02 | 1.019 | 1.018 | 1.02 | 963
The Drove Exports | 1.038 | 1.035 | 1.029 | 1.033 | 7306
Water Lane Exports | 1.017 | 1.02 | 1.012 | 1.02 | 7320
Plymouth Rock Exports | 1.014 | 1.014 | 1.012 | 1.014 | 7342
Barton Hill Exports | 1.014 | 1.014 | 1.012 | 1.014 | 7318

## SWAE - Annex 5 LLFs
These line loss factors have been audited by Elexon in accordance with BSCP128. The line loss factors that are approved by the BSC Panel consequently published on the Elexon website will take precedence and will be used in Settlement.
Western Power Distribution (South Wales) plc - LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Peak | Winter | Night | Other
Monday to Friday Mar to Oct |  |  | 00:30 - 07:30 | 00:00 - 00:30 07:30 - 24:00
Monday to Friday Nov to Feb | 16:00 – 19:00 | 07:30 – 16:00 | 00:30 - 07:30 | 00:00 - 00:30 19:00 - 24:00
Saturday and Sunday All Year |  |  | 00:30 - 07:30 | 00:00 - 00:30 07:30 - 24:00
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
132kV connected | 1.009 | 1.008 | 1.006 | 1.007
132/EHV connected | 1.013 | 1.013 | 1.012 | 1.013
132/HV connected | 1.015 | 1.015 | 1.014 | 1.014
EHV connected | 1.024 | 1.024 | 1.022 | 1.023 | 596, 699
High Voltage Substation | 1.032 | 1.031 | 1.03 | 1.03 | 444, 605, 607
High Voltage Network | 1.041 | 1.039 | 1.032 | 1.036 | 95, 96, 400, 606, 698
Low Voltage Substation | 1.059 | 1.057 | 1.057 | 1.056 | 93, 94, 344, 602, 604, 717
Low Voltage Network | 1.077 | 1.072 | 1.067 | 1.069 | 91, 92, 100, 101, 105, 106, 116, 117, 194, 200, 201, 294, 300, 603, 697, 700, 701, 718, 719, 720, 800, 801, 810, 811, 843, 860, 861, 862, 863
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Mynydd Y Bwllfa WF | 1.009 | 1.008 | 1.006 | 1.007 | 419
Western Wood 2 Biomass | 1.009 | 1.008 | 1.006 | 1.007 | 420
Mynydd Y Gwair WF Import | 1.009 | 1.008 | 1.006 | 1.007 | 421
Penrhiwarwydd Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 460
Cwmbargoed Coal Washery | 1.032 | 1.033 | 1.032 | 1.032 | 461
Little Neath PV | 1.024 | 1.024 | 1.022 | 1.023 | 462
Hoplass Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 463
Gelliwern Isaf PV | 1.024 | 1.024 | 1.022 | 1.023 | 464
Oak Cottage PV | 1.024 | 1.024 | 1.022 | 1.023 | 465
Red Court Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 466
Carn Nicholas PV | 1.024 | 1.024 | 1.022 | 1.023 | 467
Brynwhilach Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 468
Pant Y Moch PV Boundary | 1.024 | 1.024 | 1.022 | 1.023 | 469
Jesus College PV | 1.024 | 1.024 | 1.022 | 1.023 | 470
Sully Moors STOR | 1.024 | 1.024 | 1.022 | 1.023 | 471
Hafod y Dafal PV | 1.024 | 1.024 | 1.022 | 1.023 | 472
Dowlais 2 Import (do not use) | 1.024 | 1.024 | 1.022 | 1.023 | 473
Stormydown AD Plant 1 | 1.024 | 1.024 | 1.022 | 1.023 | 474
Stormydown AD Plant 2 | 1.024 | 1.024 | 1.022 | 1.023 | 475
Stormy Down PV | 1.024 | 1.024 | 1.022 | 1.023 | 476
Oak Grove Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 477
Llancadle Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 478
Lower House Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 479
Derwyn PV | 1.024 | 1.024 | 1.022 | 1.023 | 480
Rosedew PV | 1.024 | 1.024 | 1.022 | 1.023 | 481
Pen Rhiw Caradog PV | 1.024 | 1.024 | 1.022 | 1.023 | 482
Mynydd Y Gwrhyd WF | 1.024 | 1.024 | 1.022 | 1.023 | 483
Tonypandy STOR | 1.024 | 1.038 | 1.038 | 1.038 | 484
Traston Road STOR | 1.024 | 1.003 | 1.003 | 1.003 | 485
Maesgwyn Extension WF | 1.024 | 1.024 | 1.022 | 1.023 | 486
Manor Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 487
Pant Y Moch PV Site 1 | 1.024 | 1.024 | 1.022 | 1.023 | 488
Rhewl Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 489
Pant Y Moch PV Site 2 | 1.024 | 1.024 | 1.022 | 1.023 | 490
Bargoed PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 491
Mynydd Brombil WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 492
Rassau Ind Est STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 493
Llynfi Afan WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 494
Mynydd Yr Aber WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 495
Waun Y Pound 1 STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 496
Cockett Valley PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 497
Nathenfoel PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 498
Waun Y Pound 2 STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 499
St Peters Church WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 500
Corus Trostre | 1.007 | 1.007 | 1.007 | 1.007 | 504
Corus Orb | 1.003 | 1.003 | 1.003 | 1.003 | 505
ABB Cornelly | 1.024 | 1.024 | 1.022 | 1.023 | 507
Bettws | 1.009 | 1.008 | 1.006 | 1.007 | 508
Blaen Bowi | 1.024 | 1.024 | 1.022 | 1.023 | 509
Alpha Steel | 1 | 1 | 1 | 1 | 510
BOC Margam | 1.001 | 1.001 | 1.001 | 1.001 | 511
Ford Bridgend | 1.004 | 1.004 | 1.004 | 1.004 | 512
Alcoa | 1.003 | 1.003 | 1.003 | 1.003 | 513
ASW Rod Mill | 1.002 | 1.002 | 1.003 | 1.003 | 514
Total Fina Elf | 1.007 | 1.007 | 1.007 | 1.007 | 515
PCC Texaco | 1.005 | 1.005 | 1.005 | 1.005 | 517
Whitbread Magor | 1.004 | 1.004 | 1.004 | 1.004 | 518
Mainline Pipelines | 1.01 | 1.01 | 1.01 | 1.01 | 519
ASW 33kV | 1.006 | 1.006 | 1.006 | 1.006 | 520
Blue Circle Cement | 1.005 | 1.005 | 1.006 | 1.006 | 522
Inco | 1.003 | 1.003 | 1.003 | 1.003 | 529
Swansea University | 1.009 | 1.009 | 1.008 | 1.008 | 531
DCWW Nantgaredig | 1.025 | 1.026 | 1.032 | 1.029 | 532
Fort James | 1.013 | 1.012 | 1.013 | 1.013 | 533
BORDEN | 1.004 | 1.004 | 1.004 | 1.004 | 534
SOLUTIA | 1.003 | 1.003 | 1.003 | 1.003 | 535
Dow Corning | 1.002 | 1.002 | 1.002 | 1.002 | 536
DCWW Rover Way | 1.001 | 1.001 | 1.001 | 1.001 | 538
Simms Metals | 1.001 | 1.001 | 1.001 | 1.001 | 539
Milford Energy Import | 1.01 | 1.01 | 1.01 | 1.01 | 541
South Hook | 1.006 | 1.006 | 1.007 | 1.007 | 542
FELINDRE | 1.001 | 1.001 | 1.001 | 1.001 | 545
TIMET | 1.003 | 1.003 | 1.003 | 1.003 | 546
Blaen Cregan | 1.024 | 1.024 | 1.022 | 1.023 | 547
Blaengwen Wind Farm | 1.009 | 1.008 | 1.006 | 1.007 | 548
Bryn Titli Wind Farm | 1.024 | 1.024 | 1.022 | 1.023 | 549
Crymlin Burrows | 1.008 | 1.008 | 1.008 | 1.008 | 571
Dyffryn Brodyn Wind Farm | 1.024 | 1.024 | 1.022 | 1.023 | 572
Fochriw | 1.024 | 1.024 | 1.022 | 1.023 | 573
Llyn Brianne | 1.024 | 1.024 | 1.022 | 1.023 | 574
Maerdy | 1.024 | 1.024 | 1.022 | 1.023 | 575
Hirwaun GE Rhigos Rd LF Import | 1.024 | 1.024 | 1.022 | 1.023 | 576
Margam Biomass | 1.024 | 1.024 | 1.022 | 1.023 | 577
Newport Biomass | 1.009 | 1.008 | 1.006 | 1.007 | 578
Pwllfa Watkin | 1.024 | 1.024 | 1.022 | 1.023 | 579
Taff Ely Wind Farm | 1.024 | 1.024 | 1.022 | 1.023 | 580
Trecatti | 1.024 | 1.024 | 1.022 | 1.023 | 581
Withyhedges Landfill | 1.024 | 1.024 | 1.022 | 1.023 | 582
Parc Cynog | 1.024 | 1.024 | 1.022 | 1.023 | 583
Parc Cynog (Pendine) | 1.024 | 1.024 | 1.022 | 1.023 | 584
Maesgwyn | 1.009 | 1.008 | 1.006 | 1.007 | 585
Ferndale | 1.024 | 1.024 | 1.022 | 1.023 | 586
Pant y Wal WF | 1.024 | 1.024 | 1.022 | 1.023 | 587
Mynydd Portref | 1.024 | 1.024 | 1.022 | 1.023 | 588
Newton Down | 1.024 | 1.024 | 1.022 | 1.023 | 589
Tiers Cross PV | 1.009 | 1.008 | 1.006 | 1.007 | 590
Llynfi Biomass | 1.009 | 1.008 | 1.006 | 1.007 | 591
Thyssenkruup Camford Pressing | 1.032 | 1.031 | 1.03 | 1.03 | 593
Hoover | 1.032 | 1.031 | 1.03 | 1.03 | 594
Berthllwyd PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 610
Alcoa B STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 611
Whitton Mawr PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 612
Barry Dock Biomass Import | 1.024 | 1.024 | 1.022 | 1.023 | 613
North Tenement PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 614
Bryncyrnau Isaf PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 615
University Hospital of Wales | 1.032 | 1.031 | 1.03 | 1.03 | 620
MOD Qinetiq | 1.032 | 1.031 | 1.03 | 1.03 | 622
Western Coal | 1.023 | 1.023 | 1.023 | 1.023 | 623
Tregaron | 1.032 | 1.031 | 1.03 | 1.03 | 625
Waunarlydd STOR | 1.024 | 1.024 | 1.022 | 1.023 | 627
Briton Ferry STOR | 1.024 | 1.024 | 1.022 | 1.023 | 628
Hirwaun STOR | 1.024 | 1.024 | 1.022 | 1.023 | 629
Ffos Las PV | 1.024 | 1.024 | 1.022 | 1.023 | 631
Pont Andrew PV | 1.024 | 1.024 | 1.022 | 1.023 | 632
Beaufort Power STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 634
Brecon Power STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 671
Bryn Blaen WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 680
Brechfa Forest West WF Import | 1.009 | 1.008 | 1.006 | 1.007 | 750
Pen Y Cymoedd WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 760
Afan Way STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 761
Manmoel PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 762
Maesgwyn Extension PV Import | 1.024 | 1.024 | 1.022 | 1.023 | 763
Crumlin STOR Import | 1.024 | 1.024 | 1.022 | 1.023 | 764
Pen Bryn Oer WF Import | 1.024 | 1.024 | 1.022 | 1.023 | 765
Tata Margam Grange | 1 | 1 | 1 | 1 | 880
Tata Margam CefnG | 1.024 | 1.024 | 1.022 | 1.023 | 881
Tir John STOR | 1.024 | 1.024 | 1.022 | 1.023 | 882
Wear Point WF | 1.024 | 1.024 | 1.022 | 1.023 | 883
West Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 884
Jordanston Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 885
Rudbaxton PV | 1.024 | 1.024 | 1.022 | 1.023 | 886
Wogaston Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 887
Dowlais STOR | 1.024 | 1.024 | 1.022 | 1.023 | 888
Trident Park Recovery | 1.024 | 1.024 | 1.022 | 1.023 | 890
Baglan Bay PV | 1.024 | 1.024 | 1.022 | 1.023 | 891
Caermelyn PV | 1.024 | 1.024 | 1.022 | 1.023 | 892
Liddlestone Ridge PV | 1.024 | 1.024 | 1.022 | 1.023 | 893
Garn Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 894
Llandarcy STOR | 1.024 | 1.024 | 1.022 | 1.023 | 895
Treguff Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 896
Loughor Solar Park | 1.024 | 1.024 | 1.022 | 1.023 | 897
Sutton Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 898
Cefn Betingau PV | 1.024 | 1.024 | 1.022 | 1.023 | 899
Clawdd Ddu PV | 1.024 | 1.024 | 1.022 | 1.023 | 900
Pentre Solar Farm | 1.024 | 1.024 | 1.022 | 1.023 | 901
Barry STOR | 1.024 | 1.024 | 1.022 | 1.023 | 902
Fenton Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 903
Yerbeston Gate Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 904
Pen Y Cae PV | 1.024 | 1.024 | 1.022 | 1.023 | 905
Saron PV | 1.024 | 1.024 | 1.022 | 1.023 | 906
Hendre Fawr PV | 1.024 | 1.024 | 1.022 | 1.023 | 907
Hendai Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 908
Cwm Cae Singrug PV | 1.024 | 1.024 | 1.022 | 1.023 | 909
Brynteg Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 910
Court Coleman PV | 1.024 | 1.024 | 1.022 | 1.023 | 911
Llwyndu Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 912
Stormydown Boundary | 1.024 | 1.024 | 1.022 | 1.023 | 913
Abergelli Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 914
Crug Mawr Farm PV | 1.024 | 1.024 | 1.022 | 1.023 | 915
Yerbeston Chapel Hill PV | 1.024 | 1.024 | 1.022 | 1.023 | 916
Aberaman Park Phase 2 | 1.024 | 1.024 | 1.022 | 1.023 | 917
Rhyd-y-Pandy PV | 1.024 | 1.024 | 1.022 | 1.023 | 918
Haverfordwest PV | 1.024 | 1.024 | 1.022 | 1.023 | 919
Blaenlliedi Farm WF | 1.024 | 1.024 | 1.022 | 1.023 | 920
Centrica, Barry, Turbines & Station Demand | 1.002 | 1.002 | 1.002 | 1.002 | 7051
Centrica Barry Standby | 1.041 | 1.039 | 1.032 | 1.036 | 7055
Solutia District Energy Newport | 1.002 | 1.003 | 1.003 | 1.003 | 7159
Aberdare District Energy | 1.009 | 1.015 | 1.018 | 1.017 | 7163
Dowlais II (Import) | 1.024 | 1.024 | 1.023 | 1.023 | 7328
Alcoa (Import) | 1.024 | 1.024 | 1.022 | 1.023 | 7346
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Mynydd Y Bwllfa WF Export | 1.011 | 1.011 | 1.011 | 1.011 | 425
Western Wood 2 Biomass Export | 1.009 | 1.008 | 1.006 | 1.007 | 426
Mynydd Y Gwair WF EXport | 1.009 | 1.008 | 1.006 | 1.007 | 427
Tata Margam CefnG Export | 1.001 | 1.024 | 1.022 | 1.023 | 601
Solutia Export | 1.015 | 1.015 | 1.014 | 1.014 | 617
Total Fina Elf Export | 1.015 | 1.015 | 1.014 | 1.014 | 618
Whitbread Magor Export | 1.015 | 1.015 | 1.014 | 1.014 | 619
Tower Export | 1.024 | 1.024 | 1.022 | 1.023 | 621
Fort James Export | 1.032 | 1.031 | 1.03 | 1.03 | 633
Dow Corning Export | 1.002 | 1.002 | 1.002 | 1.002 | 636
Pont Andrew PV Export | 1.024 | 1.027 | 1.022 | 1.027 | 642
Ffos Las PV Export | 1.024 | 1.028 | 1.022 | 1.028 | 643
Hirwaun STOR Export | 1.019 | 1.024 | 1.022 | 1.023 | 644
Briton Ferry STOR Export | 1.007 | 1.024 | 1.022 | 1.023 | 645
Waunarlydd STOR Export | 1.011 | 1.024 | 1.022 | 1.023 | 646
Trostrey Court Export | 1.032 | 1.031 | 1.03 | 1.03 | 647
Llynfi Biomass Export | 1.009 | 1.008 | 1.006 | 1.007 | 648
Tiers Cross PV Export | 1.006 | 1.006 | 1.006 | 1.006 | 649
Taff Ely Wind Farm Export | 1.02 | 1.019 | 1.021 | 1.02 | 650
Bryn Titli Wind Farm Export | 1.099 | 1.099 | 1.099 | 1.098 | 651
Dyffryn Brodin Wind Farm Exp | 1.035 | 1.034 | 1.036 | 1.036 | 652
Llyn Brianne Export | 1.016 | 1.017 | 1.031 | 1.034 | 653
Tregaron Export | 1.032 | 1.031 | 1.03 | 1.03 | 658
Parc Cynog Export | 1.025 | 1.023 | 1.026 | 1.023 | 659
Blaen Bowi Export | 1.021 | 1.021 | 1.021 | 1.021 | 660
MARGAM BIOMASS Export | 0.992 | 0.993 | 0.992 | 0.992 | 661
Trecatti Export | 1.028 | 1.028 | 1.028 | 1.028 | 662
Blaen Cregan Wind Farm Export | 1.008 | 1.007 | 1.008 | 1.009 | 663
ABB Cornelly Export | 1.006 | 1.008 | 1.009 | 1.009 | 664
Crymlin Burrows Export | 1.024 | 1.024 | 1.022 | 1.023 | 665
Withyhedges Landfill Export | 1.035 | 1.036 | 1.036 | 1.036 | 666
Parc Cynog (Pendine) | 1.022 | 1.022 | 1.023 | 1.023 | 667
BLAENGWEN WIND FARM EXPORT | 0.999 | 0.999 | 0.999 | 0.999 | 668
Pwllfa Watkin Export | 1.025 | 1.026 | 1.026 | 1.026 | 670
Bettws Export | 1.003 | 1.003 | 1.004 | 1.004 | 674
Fochriw EHV Export | 1.024 | 1.024 | 1.022 | 1.023 | 675
Maerdy Export | 1.017 | 1.017 | 1.02 | 1.02 | 676
Newport Biomass Export | 1.009 | 1.008 | 1.006 | 1.007 | 677
Milford Energy Export | 1.004 | 1.005 | 1.005 | 1.005 | 678
Ferndale Export | 1.033 | 1.033 | 1.033 | 1.033 | 679
Maesgwyn Export | 1.011 | 1.011 | 1.011 | 1.011 | 684
Pant y Wal WF Export | 0.999 | 0.998 | 1.001 | 1.001 | 685
Mynydd Portref Export | 1.02 | 1.019 | 1.021 | 1.021 | 686
Newton Down Export | 1.006 | 1.006 | 1.007 | 1.007 | 687
Oak Grove Farm PV Export | 1.024 | 1.01 | 1.022 | 1.01 | 721
Llancadle Farm PV Export | 1.024 | 1.009 | 1.022 | 1.009 | 722
Lower House Farm PV Export | 1.024 | 1.031 | 1.022 | 1.031 | 723
Derwyn PV Export | 1.024 | 1.004 | 1.022 | 1.004 | 724
Rosedew PV Export | 1.024 | 1.018 | 1.022 | 1.018 | 725
Pen Rhiw Caradog PV Export | 1.024 | 1.018 | 1.022 | 1.018 | 726
Mynydd Y Gwrhyd WF Export | 1.018 | 1.018 | 1.019 | 1.019 | 727
Tonypandy STOR Export | 1.03 | 1.036 | 1.038 | 1.037 | 728
Traston Road STOR Export | 1.002 | 1.002 | 1.003 | 1.003 | 729
Maesgwyn Extension WF Export | 1.024 | 1.024 | 1.022 | 1.023 | 730
Manor Farm PV Export | 1.024 | 1.025 | 1.022 | 1.025 | 731
Pant Y Moch PV Site 1 Export | 1.024 | 1.024 | 1.022 | 1.023 | 732
Rhewl Farm PV Export | 1.024 | 1.012 | 1.022 | 1.012 | 733
Pant Y Moch PV Site 2 Export | 1.024 | 1.024 | 1.022 | 1.023 | 734
Bargoed PV Export | 1.024 | 1.034 | 1.022 | 1.034 | 735
Mynydd Brombil WF Export | 1.019 | 1.019 | 1.02 | 1.02 | 736
Rassau Ind Est STOR Export | 0.998 | 1.007 | 1.008 | 1.007 | 737
Llynfi Afan WF Export | 0.995 | 0.994 | 0.995 | 0.996 | 738
Mynydd Yr Aber WF Export | 1.024 | 1.024 | 1.022 | 1.023 | 739
Waun Y Pound 1 STOR Export | 1.001 | 1.005 | 1.005 | 1.005 | 740
Cockett Valley PV Export | 1.024 | 1.009 | 1.022 | 1.009 | 741
Nathenfoel PV Export | 1.024 | 1.002 | 1.022 | 1.002 | 742
Waun Y Pound 2 STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 743
St Peters Church WF Export | 0.993 | 0.992 | 0.995 | 0.994 | 744
Berthllwyd PV Export | 1.024 | 1.011 | 1.022 | 1.011 | 745
Alcoa B STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 746
Whitton Mawr PV Export | 1.024 | 1.007 | 1.022 | 1.007 | 747
Barry Dock Biomass Export | 1.024 | 1.024 | 1.022 | 1.023 | 748
North Tenement PV Export | 1.024 | 1.018 | 1.022 | 1.018 | 749
Bryncyrnau Isaf PV Export | 1.024 | 1.019 | 1.022 | 1.019 | 772
Hirwaun GE Rhigos Rd LF Export | 1.024 | 1.024 | 1.022 | 1.023 | 773
Manmoel PV Export | 1.024 | 1.013 | 1.022 | 1.014 | 774
Maesgwyn Extension PV Export | 1.024 | 1.024 | 1.022 | 1.023 | 775
Crumlin STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 776
Pen Bryn Oer WF Export | 1.024 | 1.024 | 1.022 | 1.023 | 777
Ford Bridgend WT Export | 1.009 | 1.008 | 1.006 | 1.007 | 778
Brechfa Forest West WF Export | 1.009 | 1.008 | 1.006 | 1.007 | 779
DCWW Rover Way Export | 1.015 | 1.015 | 1.014 | 1.014 | 786
Tata Margam Grange Export | 1.024 | 1.024 | 1.022 | 1.023 | 788
Afan Way STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 789
Tir John STOR Export | 1.007 | 1.024 | 1.022 | 1.023 | 790
West Farm PV Export | 1.024 | 1.003 | 1.022 | 1.003 | 791
Jordanston Farm PV Export | 1.024 | 1.032 | 1.022 | 1.031 | 792
Rudbaxton PV Export | 1.024 | 1.031 | 1.022 | 1.031 | 793
Brecon Power STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 921
Beaufort Power STOR Export | 1.024 | 1.024 | 1.022 | 1.023 | 922
Wear Point WF Export | 1.005 | 1.005 | 1.005 | 1.005 | 940
Wogaston Farm PV Export | 1.024 | 1.024 | 1.022 | 1.023 | 941
Dowlais STOR Export | 1.023 | 1.024 | 1.022 | 1.023 | 942
Hoplass Parm PV Export | 1.024 | 1.001 | 1.022 | 1 | 943
Trident Park Recovery Export | 0.998 | 0.998 | 0.998 | 0.998 | 944
Baglan Bay PV Exports | 1.024 | 1.024 | 1.022 | 1.007 | 945
Caermelyn PV Exports | 1.087 | 1.073 | 1.022 | 1.07 | 946
Liddlestone Ridge PV Exports | 1.024 | 1.032 | 1.022 | 1.031 | 947
Garn Farm PV Export | 1.024 | 1.012 | 1.022 | 1.012 | 948
Llandarcy STOR Export | 1.009 | 1.024 | 1.022 | 1.014 | 949
Treguff Farm PV Export | 1.024 | 1.014 | 1.022 | 1.013 | 950
Loughor Solar Park Export | 1.024 | 1.008 | 1.022 | 1.008 | 951
Sutton Farm PV Export | 1.024 | 1.004 | 1.022 | 1.004 | 952
Cefn Betingau PV Export | 1.024 | 1.002 | 1.022 | 1.002 | 953
Clawdd Ddu PV Export | 1.024 | 1.009 | 1.022 | 1.009 | 954
Pentre Solar Farm Export | 1.024 | 1.026 | 1.022 | 1.025 | 955
Barry STOR Export | 1.012 | 1.018 | 1.022 | 1.018 | 956
Fenton Farm PV Export | 1.017 | 1.015 | 1.017 | 1.014 | 957
Yerbeston Gate Farm PV Export | 1.024 | 1.038 | 1.022 | 1.037 | 958
Pen Y Cae PV Export | 1.024 | 1.008 | 1.022 | 1.008 | 959
Saron PV Export | 1.024 | 1.008 | 1.022 | 1.008 | 960
Hendre Fawr PV Export | 1.024 | 1.02 | 1.022 | 1.019 | 961
Hendai Farm PV Export | 1.024 | 1.04 | 1.022 | 1.039 | 962
Cwm Cae Singrug PV Export | 1.024 | 1.015 | 1.022 | 1.015 | 963
Brynteg Farm PV Export | 1.022 | 1.02 | 1.022 | 1.02 | 964
Court Coleman PV Export | 1.007 | 1.005 | 1.022 | 1.005 | 965
Llwyndu Farm PV Export | 1.024 | 1.051 | 1.022 | 1.05 | 966
Stormydown Boundary Export | 1.007 | 1.007 | 1.007 | 1.007 | 967
Abergelli Farm PV Export | 1.024 | 1 | 1.022 | 1 | 968
Crug Mawr Farm PV Export | 1.024 | 1.073 | 1.022 | 1.072 | 969
YerbestonChapelHill PV Export | 1.024 | 1.002 | 1.022 | 1.001 | 970
Aberaman Park Phase 2 Export | 1.005 | 1.017 | 1.018 | 1.016 | 971
Rhyd-y-Pandy PV Export | 1.024 | 1.002 | 1.022 | 1.002 | 972
Haverfordwest PV Export | 1.017 | 1.016 | 1.022 | 1.016 | 973
Blaenlliedi Farm WF Export | 1.027 | 1.027 | 1.027 | 1.027 | 974
Penrhiwarwydd Farm PV Export | 1.024 | 1.018 | 1.022 | 1.017 | 975
Little Neath PV Export | 1.024 | 1.002 | 1.022 | 1.002 | 976
Gelliwern Isaf PV Export | 1.024 | 1.006 | 1.022 | 1.006 | 977
Oak Cottage PV Export | 1.024 | 1.016 | 1.022 | 1.016 | 978
Red Court Farm PV Export | 1.024 | 1.006 | 1.022 | 1.006 | 979
Carn Nicholas PV Export | 1.024 | 1.024 | 1.022 | 1.023 | 980
Brynwhilach Farm PV Export | 1.024 | 1.001 | 1.022 | 1.001 | 981
Pant Y Moch PV Boundary Export | 1.024 | 1.024 | 1.022 | 1.023 | 982
Jesus College PV Export | 1.024 | 1.004 | 1.022 | 1.004 | 983
Sully Moors STOR Export | 0.994 | 1.002 | 1.003 | 1.001 | 984
Hafod y Dafal PV Export | 1.024 | 1.014 | 1.022 | 1.014 | 985
Dowlais 2 Export (do not use) | 1.024 | 1.024 | 1.022 | 1.023 | 986
Stormydown AD Plant 1 Export | 1.024 | 1.024 | 1.022 | 1.023 | 987
Stormydown AD Plant 2 Export | 1.024 | 1.024 | 1.022 | 1.023 | 988
Stormy Down PV Export | 1.024 | 1.006 | 1.022 | 1.006 | 989
Bryn Blaen WF Export | 1.024 | 1.024 | 1.022 | 1.023 | 990
Dowlais II (Export) | 1.016 | 1.022 | 1.023 | 1.022 | 7329
Alcoa (Export) | 1.024 | 1.024 | 1.022 | 1.023 | 7347

## MIDE - Annex 5 LLFs
These line loss factors have been audited by Elexon in accordance with BSCP128. The line loss factors that are approved by the BSC Panel consequently published on the Elexon website will take precedence and will be used in Settlement.
Western Power Distribution (West Midlands) plc - LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Peak | Winter | Night | Other
Monday to Friday Mar to Oct |  |  | 00:30 – 07:30 | 07:30 – 00:30
Monday to Friday Nov to Feb | 16:00 – 19:00 | 07:30 – 16:00 19:00 – 20:00 | 00:30 – 07:30 | 20:00 – 00:30
Saturday and Sunday All Year |  |  | 00:30 – 07:30 | 07:30 – 00:30
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
132kV connected | 1.002 | 1.002 | 1.002 | 1.002
132/EHV connected | 1.007 | 1.006 | 1.007 | 1.006
132/HV connected | 1.008 | 1.008 | 1.008 | 1.008
EHV connected | 1.015 | 1.014 | 1.011 | 1.012
High Voltage Substation | 1.022 | 1.021 | 1.017 | 1.019
High Voltage Network | 1.048 | 1.044 | 1.03 | 1.037 | 23, 145, 146, 322, 323, 365, 367, 575, 577
Low Voltage Substation | 1.066 | 1.063 | 1.055 | 1.057 | 19, 128, 143, 144, 570, 572, 574
Low Voltage Network | 1.083 | 1.077 | 1.065 | 1.07 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 20, 21, 22, 24, 25, 26, 27, 30, 34, 35, 36, 40, 41, 42, 46, 47, 49, 85, 86, 87, 88, 95, 96, 97, 98, 99, 107, 108, 109, 110, 111, 112, 121, 124, 127, 129, 132, 141, 142, 571, 573, 625, 626, 632, 633
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Hayford Fm Substation (LV Imp) | 1.083 | 1.077 | 1.065 | 1.07 | 628
Troughton Farm PV (Import) | 1.002 | 1.002 | 1.002 | 1.002 | 636
Tyseley Waste Import | 1.002 | 1.002 | 1.001 | 1.001 | 702
Takao Europe | 1.014 | 1.014 | 1.014 | 1.014 | 704
Four Ashes Incinerator Import | 1.015 | 1.014 | 1.011 | 1.012 | 705
Witches Farm Solar Import | 1.015 | 1.014 | 1.011 | 1.012 | 706
Uni of Birmingham Import | 1.006 | 1.006 | 1.006 | 1.006 | 707
South Staffs Water Import | 1.054 | 1.056 | 1.057 | 1.056 | 709
Wolverhampton WS Import | 1.015 | 1.014 | 1.011 | 1.012 | 710
Stoke CHP Import | 1.005 | 1.005 | 1.005 | 1.005 | 711
WBB Minerals Import | 1.015 | 1.014 | 1.011 | 1.012 | 712
Cauldon Cement Import | 1.034 | 1.035 | 1.039 | 1.039 | 713
Abson Gas Compressor Import | 1.015 | 1.014 | 1.026 | 1.012 | 714
Ervin Amasteel Import | 1.001 | 1.001 | 1.001 | 1.001 | 715
Hanford Waste Services Import | 1.015 | 1.014 | 1.011 | 1.012 | 716
NR Kidsgrove Import | 1.015 | 1.015 | 1.015 | 1.015 | 717
NR Stafford Import | 1.037 | 1.037 | 1.037 | 1.037 | 718
NR Nechells/Washwood Heath Imp | 1.001 | 1.001 | 1.001 | 1.001 | 719
NR Winson Green Import | 1.002 | 1.002 | 1.002 | 1.002 | 720
NR Smethwick Import | 1 | 1 | 1 | 1 | 721
NR Willenhall Import | 1 | 1 | 1 | 1 | 722
Northwick Import | 1.022 | 1.021 | 1.017 | 1.019 | 723
Inco Alloys | 1.022 | 1.021 | 1.017 | 1.019 | 724
Swancote Energy Import | 1.015 | 1.014 | 1.011 | 1.012 | 725
Springhill Solar Park Import | 1.022 | 1.021 | 1.017 | 1.019 | 726
NG Gas Wormington | 1.022 | 1.021 | 1.017 | 1.019 | 727
Greenfrog STOR Import | 1.022 | 1.021 | 1.017 | 1.019 | 728
Union Road/EMR Oldbury Import | 1.001 | 1.001 | 1.001 | 1.001 | 729
Quatt Import | 1.022 | 1.021 | 1.017 | 1.019 | 730
Knypersley Import | 1.022 | 1.021 | 1.017 | 1.019 | 740
Simplex Import | 1.022 | 1.021 | 1.017 | 1.019 | 742
Northwick STOR sub supply | 1.022 | 1.021 | 1.017 | 1.019 | 743
Star Aluminium Import | 1.022 | 1.021 | 1.017 | 1.019 | 744
Goodyear | 1.006 | 1.006 | 1.006 | 1.006 | 747
Battlefield Generation Import | 1.019 | 1.019 | 1.011 | 1.012 | 770
Says Farm PV Import | 1.015 | 1.014 | 1.011 | 1.012 | 771
Hayford Fm PV Embedded 2 (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 772
Rotherdale Farm PV Import | 1.028 | 1.028 | 1.028 | 1.028 | 773
Lower Newton Solar Farm (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 774
Wrockwardine Solar Farm (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 775
Condover Solar Farm (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 776
Tower Hill Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 777
Hill House Farm Solar (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 778
Pitchford Farm Solar (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 779
Sundorne Solar Park (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 780
Hartlebury EFW (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 781
Upper Huntingford PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 782
Ring O Bells Solar (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 783
Hall Farm PV Awre (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 784
Northwick 5 Mile Dr PV Import | 1.022 | 1.021 | 1.017 | 1.019 | 785
Greenfrog STOR Extens (Import) | 1.022 | 1.021 | 1.017 | 1.019 | 786
Wickhamford PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 794
Yorkley Wood Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 795
Awbridge Farm Diesel Gen (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 796
Bristol Rd Glos STOR (Import) | 1.015 | 1.015 | 1.015 | 1.015 | 797
Actrees Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 798
Sheriffhales Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 799
Upper Wick Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 801
Astley Solar Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 866
Hayford Fm PV Embedded 1 (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 867
Sheriffhales CIC PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 868
Wolverhampton Power STOR (Imp) | 1.015 | 1.001 | 1.011 | 1.012 | 869
Moneystone Quarry PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 870
Heywood Grange Fm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 871
Garreg Lwyd WF (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 872
Henley Solar Farm PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 873
Sudmeadow Rd Gen STOR (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 874
High Point Solar PV (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 875
Staunch Standby STOR (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 876
ISIS House STOR (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 877
Heywood Grange Bttry (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 878
Upper Meadowly Farm PV(Import) | 1.015 | 1.014 | 1.011 | 1.012 | 879
Javelin Park EFW (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 880
Rock Farm ESS (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 881
Bloxwich ESS (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 882
Hinksford Farm Gas (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 883
Chatterley Whitfield CHP (Imp) | 1.015 | 1.014 | 1.011 | 1.012 | 884
Larport Farm BESS (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 885
Sandwell Power STOR (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 886
Wednesbury Power STOR (Import) | 1.015 | 1.014 | 1.011 | 1.012 | 887
Havannah Mills | 1.048 | 1.044 | 1.03 | 1.037 | 39
Cellarhead - Meaford | 1.009 | 1.009 | 1.009 | 1.009 | 2226
Stanner | 1.048 | 1.044 | 1.03 | 1.037 | 2818
Rugeley Power Station | 1 | 1 | 1 | 1 | 4018
Fort Dunlop LV Import | 1.083 | 1.077 | 1.065 | 1.07 | 7177
Cambridge Arms | 1.002 | 1.002 | 1.002 | 1.002 | 7294
Sudmeadow Rd STOR (Imps) | 1.015 | 1.009 | 1.009 | 1.009 | 7337
Bloxwich ESS (Imps) | 1.015 | 1.014 | 1.011 | 1.012 | 7371
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Tyseley Waste Export | 1.001 | 1.001 | 1.001 | 1.001 | 703
Uni of Birmingham Export | 1.002 | 1.002 | 1.002 | 1.002 | 708
Quatt Export | 1.022 | 1.021 | 1.017 | 1.019 | 731
Wolverhampton WS Export | 0.999 | 0.999 | 0.999 | 0.999 | 732
Stoke CHP Export | 1.015 | 1.014 | 1.011 | 1.012 | 733
Hanford Waste Services Export | 1.003 | 1.003 | 1.003 | 1.003 | 734
NR Kidsgrove Export | 1.015 | 1.015 | 1.015 | 1.015 | 735
NR Stafford Export | 1.037 | 1.037 | 1.011 | 1.037 | 736
NR Winson Green Export | 1.015 | 1.014 | 1.011 | 1.012 | 737
NR Smethwick Export | 1 | 1 | 1.011 | 1 | 738
NR Willenhall Export | 1 | 1 | 1.011 | 1 | 739
NR Nechells/Washwood Heath Exp | 1 | 1 | 1 | 1 | 741
Redditch Gas Turbine Export | 1.022 | 1.021 | 1.017 | 1.019 | 745
Knypersley Export | 1.022 | 1.021 | 1.017 | 1.019 | 746
Northwick Export | 1.022 | 1.021 | 1.017 | 1.019 | 748
Swancote Energy Export | 1.057 | 1.057 | 1.056 | 1.056 | 749
Four Ashes Incinerator Export | 0.994 | 0.994 | 0.994 | 0.994 | 750
Witches Farm Solar Export | 1.015 | 1.055 | 1.011 | 1.054 | 751
Springhill Solar Park Export | 1.022 | 1.021 | 1.017 | 1.019 | 752
Greenfrog STOR Export | 1.022 | 1.021 | 1.017 | 1.019 | 753
Union Road/EMR Oldbury Export | 1.001 | 1.001 | 1.011 | 1.012 | 754
Battlefield Generation Export | 1.017 | 1.017 | 1.017 | 1.017 | 755
Says Farms PV Export | 1.015 | 1.022 | 1.011 | 1.021 | 756
Hayford Fm PV Embedded 2 (Exp) | 1.015 | 1.063 | 1.011 | 1.062 | 757
Rotherdale Farm PV Export | 1.015 | 1.028 | 1.011 | 1.028 | 758
Lower Newton Solar Farm (Exp) | 1.015 | 1.03 | 1.011 | 1.029 | 759
Wrockwardine Solar Farm (Exp) | 1.015 | 1.047 | 1.011 | 1.045 | 760
Condover Solar Farm (Export) | 1.015 | 1 | 1.011 | 0.998 | 761
Tower Hill Farm PV (Export) | 1.015 | 1.052 | 1.011 | 1.052 | 762
Hill House Farm Solar (Export) | 1.029 | 1.028 | 1.029 | 1.027 | 763
Pitchford Farm Solar (Export) | 1.015 | 1.038 | 1.044 | 1.035 | 764
Sundorne Solar Park (Export) | 1.015 | 1.02 | 1.011 | 1.02 | 765
Hartlebury EFW (Export) | 1.006 | 1.006 | 1.006 | 1.006 | 766
Upper Huntingford PV (Export) | 1.015 | 1.085 | 1.011 | 1.084 | 767
Ring O Bells Solar (Export) | 1.015 | 1.033 | 1.011 | 1.033 | 768
Hall Farm PV Awre (Export) | 1.015 | 1.036 | 1.011 | 1.036 | 769
Northwick 5 Mile Dr PV Export | 1.022 | 1.021 | 1.017 | 1.019 | 805
Greenfrog STOR Extens (Export) | 1.022 | 1.021 | 1.017 | 1.019 | 806
Wickhamford PV (Export) | 1.032 | 1.031 | 1.032 | 1.031 | 815
Yorkley Wood Farm PV (Export) | 1.015 | 1.03 | 1.011 | 1.03 | 816
Awbridge Farm Diesel Gen (Exp) | 1.015 | 1.014 | 1.011 | 1.012 | 817
Bristol Rd Glos STOR (Export) | 1.011 | 1.015 | 1.015 | 1.015 | 818
Actrees Farm PV (Export) | 1.015 | 1.062 | 1.011 | 1.061 | 819
Sheriffhales Farm PV (Export) | 1.015 | 1.022 | 1.011 | 1.022 | 820
Upper Wick Farm PV (Export) | 1.015 | 1.071 | 1.011 | 1.07 | 821
Astley Solar Farm PV (Export) | 1.015 | 1.049 | 1.011 | 1.049 | 824
Hayford Fm PV Embedded 1 (Exp) | 1.015 | 1.064 | 1.011 | 1.063 | 825
Sheriffhales CIC PV (Export) | 1.015 | 1.023 | 1.011 | 1.022 | 826
Wolverhampton Power STOR (Exp) | 0.999 | 1.001 | 1.011 | 1.001 | 827
Moneystone Quarry PV (Export) | 1.015 | 1.029 | 1.011 | 1.029 | 828
Heywood Grange Fm PV (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 829
Garreg Lwyd WF (Export) | 1.062 | 1.061 | 1.071 | 1.072 | 830
Henley Solar Farm PV (Export) | 1.015 | 1.036 | 1.011 | 1.035 | 831
Sudmeadow Rd Gen STOR (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 832
High Point Solar PV (Export) | 1.015 | 1.039 | 1.011 | 1.038 | 833
Staunch Standby STOR (Export) | 1.019 | 1.019 | 1.019 | 1.019 | 834
ISIS House STOR (Export) | 1.009 | 1.014 | 1.011 | 1.012 | 835
Heywood Grange Bttry (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 836
Upper Meadowly Farm PV(Export) | 1.015 | 1.075 | 1.011 | 1.075 | 837
Javelin Park EFW (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 838
Rock Farm Ess (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 839
Bloxwich ESS (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 840
Hinksford Farm Gas (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 841
Chatterley Whitfield CHP (Exp) | 1.015 | 1.014 | 1.011 | 1.012 | 842
Larport Farm BESS (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 843
Sandwell Power STOR (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 844
Wednesbury Power STOR (Export) | 1.015 | 1.014 | 1.011 | 1.012 | 845
Star Aluminium Export | 1.022 | 1.021 | 1.017 | 1.019 | 915
Troughton Farm PV (Export) | 1.011 | 1.011 | 1.011 | 1.011 | 933
Fort Dunlop 132kV Export | 1 | 1 | 1 | 1 | 7070
Sudmeadow Rd STOR (Exps) | 1.007 | 1.008 | 1.009 | 1.008 | 7338
Bloxwich ESS (Exps) | 1.015 | 1.014 | 1.011 | 1.012 | 7375

## EMEB - Annex 5 LLFs
These line loss factors have been audited by Elexon in accordance with BSCP128. The line loss factors that are approved by the BSC Panel consequently published on the Elexon website will take precedence and will be used in Settlement.
Western Power Distribution (East Midlands) plc - LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Peak | Winter | Night | Other
Monday to Friday Mar to Oct |  |  | 00:30 – 07:30 | 07:30 – 00:30
Monday to Friday Nov to Feb | 16:00 – 19:00 | 07:30 – 16:00 19:00 – 20:00 | 00:30 – 07:30 | 20:00 – 00:30
Saturday and Sunday All Year |  |  | 00:30 – 07:30 | 07:30 – 00:30
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
132kV connected | 1.003 | 1.003 | 1.002 | 1.002
132/EHV connected | 1.006 | 1.006 | 1.008 | 1.007
132/HV connected | 1.008 | 1.008 | 1.009 | 1.008
EHV connected | 1.014 | 1.014 | 1.012 | 1.013 | 997
High Voltage Substation | 1.02 | 1.02 | 1.019 | 1.019
High Voltage Network | 1.036 | 1.034 | 1.027 | 1.03 | 60, 90, 91, 92, 93, 94, 95, 96, 97, 98, 99, 145, 146, 929, 975, 977, 991, 996
Low Voltage Substation | 1.047 | 1.047 | 1.048 | 1.046 | 59, 80, 143, 144, 970, 972, 974
Low Voltage Network | 1.078 | 1.073 | 1.065 | 1.067 | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 16, 19, 22, 25, 28, 31, 34, 37, 40, 43, 46, 49, 52, 58, 81, 82, 83, 84, 85, 141, 142, 246, 247, 800, 801, 802, 803, 804, 821, 900, 901, 971, 973, 986, 987, 990, 993, 994, 995
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Jaguar Land Rover Gaydon (Imp) | 1.02 | 1.02 | 1.019 | 1.019 | 61
Lyon Road Gas Gen (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 155
Asher Lane 33kV STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 156
Spondon Peaking STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 157
Rhodia STOR (Import) | 1.02 | 1.02 | 1.019 | 1.019 | 280
Jaguar Land Rover Whitley(Imp) | 1.02 | 1.02 | 1.019 | 1.019 | 281
Yew Tree Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 292
Cobb Farm Egmanton PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 293
Kelmarsh Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 294
PebbleHall_Boundary_Import | 1.014 | 1.014 | 1.012 | 1.013 | 295
Copley Farm PV Claypole (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 296
Greatmoor EFW Calvert (Import) | 1.001 | 1.001 | 1.001 | 1.001 | 297
Lodge Farm (Calow) PV Import | 1.014 | 1.014 | 1.012 | 1.013 | 298
Arkwright Solar PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 299
Langar Commercial PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 300
Redfield Road 1 STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 301
Averill Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 302
Marchington Solar PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 303
West End Fm Treswell PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 304
Fields Farm Southam PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 305
Canopus Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 306
Lindridge Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 307
Thornborough Grnds PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 308
Wymeswold Narrow Lane PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 309
Manor Farm Horton PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 310
Handley Park Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 311
Shelton Lodge PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 312
Brafield on the Green PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 313
Sywell PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 314
Holtwood Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 315
Drakelow Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 316
Stragglethorpe Rd PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 317
Oxcroft Solar Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 318
Derby Waste Sinfin EFW (Imp) | 1.017 | 1.017 | 1.017 | 1.017 | 319
Littlewood Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 320
Twin Yards Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 321
Tower Hayes Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 322
The Breck Solar PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 323
Barnby Moor Retford PV(Import) | 1.014 | 1.014 | 1.012 | 1.013 | 324
Lincoln Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 325
Drakelow Renewable BIO (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 326
Tetron Point ESS (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 327
Mill Fm Gt Ponton PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 328
(PHF) Welland Bio Power Imp | 1.014 | 1.014 | 1.012 | 1.013 | 329
Deepdale Solar Fm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 330
Burton Wolds South WF (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 331
Brafield_PV_Commercial (Imps) | 1.014 | 1.014 | 1.012 | 1.013 | 332
Brafield_PV_Community (Imps) | 1.014 | 1.014 | 1.012 | 1.013 | 333
Gawcott Flds PV Commercial Imp | 1.014 | 1.014 | 1.012 | 1.013 | 334
Gawcott Flds PV Community Imp | 1.014 | 1.014 | 1.012 | 1.013 | 335
Trafalgar Pk Gas STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 336
John Brookes Sawmill BIO (Imp) | 1.016 | 1.016 | 1.016 | 1.016 | 337
Hawton Wind Farm WF (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 338
Blackbridge Farm BIO (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 339
Garnham Close STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 340
RAF Cranwell High G (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 341
Langar Community PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 342
Hermitage Lane STOR (Import) | 1.014 | 1.026 | 1.026 | 1.026 | 343
Fosse Way Radford Sem PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 344
Meadow Fm Thorpe Lang PV (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 345
Olney Hyde Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 346
Dayfields Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 347
Bolsovermoor Quarry PV(Import) | 1.014 | 1.014 | 1.012 | 1.013 | 348
Bilsthorpe PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 349
Carlton Forest STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 350
Sutton Bonnington PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 351
Alfreton Diesel Power (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 352
Green Lane Marchington PV(Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 353
Baddesley Park PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 354
Baddesley Pk Biomass (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 355
Taylor Lane 33kV STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 356
Hill Farm ESS (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 357
Leverton ESS (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 358
Nottingham Rd STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 359
Breach Farm ESS (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 361
Boston Biomass Gen AD (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 362
Twin Oaks Diesel STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 363
Colwick Private Rd STOR (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 364
Mill Fm Caythorpe ESS (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 365
(PHF) Welland Waste Imp | 1.014 | 1.014 | 1.012 | 1.013 | 366
Prestop Park Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 784
Smith Hall Farm Solar (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 785
Park Farm Solar Ashby (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 786
Aston House Solar Farm(Import) | 1.014 | 1.014 | 1.012 | 1.013 | 787
Normanton-le-Heath PV Fm (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 788
Elms Farm Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 789
Morton Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 790
Glebe Farm Podington PV-Import | 1.014 | 1.014 | 1.012 | 1.013 | 791
Rolleston Park Solar (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 792
Nowhere Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 793
Lockington Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 794
Chelveston Renewable PV-Import | 1.014 | 1.014 | 1.012 | 1.013 | 795
Horsemoor Drove Solar (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 796
Decoy Farm Crowland PV-Import | 1.014 | 1.014 | 1.012 | 1.013 | 797
Decoy Farm Crowland Bio-Import | 1.014 | 1.014 | 1.012 | 1.013 | 798
Decoy Farm Crowland AD-Import | 1.014 | 1.014 | 1.012 | 1.013 | 799
Railtrack Bytham (Import) | 1.047 | 1.047 | 1.045 | 1.046 | 824
Railtrack Grantham (Import) | 1.016 | 1.016 | 1.015 | 1.016 | 825
Railtrack Staythorpe (Import) | 1 | 1 | 1 | 1 | 826
Railtrack Retford (Import) | 1.032 | 1.032 | 1.029 | 1.031 | 827
Railtrack Rugby (Import) | 1.017 | 1.016 | 1.016 | 1.017 | 828
Railtrack Tamworth (Import) | 1.01 | 1.01 | 1.01 | 1.01 | 829
Railtrack Wolverton (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 830
Jaguar Cars | 1.02 | 1.02 | 1.019 | 1.019 | 831
Alstom Frankton | 1.02 | 1.02 | 1.019 | 1.019 | 832
University of Warwick (Import) | 1.02 | 1.02 | 1.019 | 1.019 | 833
Dunlop Factory | 1.02 | 1.02 | 1.019 | 1.019 | 834
Bombardier | 1.017 | 1.017 | 1.017 | 1.017 | 835
Corus Corby (Import) | 1.013 | 1.013 | 1.013 | 1.013 | 836
Acordis (Import) | 1.022 | 1.022 | 1.022 | 1.022 | 837
Derwent (Import) | 1.003 | 1.003 | 1.002 | 1.002 | 838
GEC Alsthom (Import) | 1.033 | 1.033 | 1.012 | 1.033 | 839
St Gobain (Import) | 1.038 | 1.038 | 1.038 | 1.038 | 840
Toyota (Import) | 1.003 | 1.004 | 1.004 | 1.004 | 841
Derby Co-Generation (Import) | 1.014 | 0.999 | 0.999 | 0.999 | 842
Rolls Royce Sinfin C (Import) | 1.014 | 1.014 | 1.012 | 0.999 | 843
ABR Foods (Import) | 1.012 | 1.012 | 1.012 | 1.012 | 844
Petsoe Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 845
Castle Cement (Import) | 1.065 | 1.064 | 1.067 | 1.066 | 846
Rugby Cement (Import) | 1.03 | 1.03 | 1.029 | 1.029 | 847
Cov & Sol Waste (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 848
Bentinck (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 849
EHV Import | 1.014 | 1.014 | 1.012 | 1.013 | 851
Asfordby 132kv | 1.001 | 1.001 | 1.001 | 1.001 | 852
Calvert Landfill (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 853
Weldon Landfill (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 854
Goosy Lodge Power (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 855
BAR Honda (Import) | 1.018 | 1.018 | 1.018 | 1.018 | 856
Burton Wolds Wind Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 857
Railtrack Bretton (Import) | 1.05 | 1.05 | 1.05 | 1.05 | 858
Bambers Farm Wind Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 859
Vine House Wind Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 860
Red House Wind Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 861
Daneshill Landfill (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 862
Corby Power (Import) | 1.014 | 1.014 | 1.014 | 1.014 | 863
Newton Longville Import | 1.014 | 1.014 | 1.012 | 1.013 | 864
Hollies Wind Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 865
Lynn Wind Farm (Import) | 1.003 | 1.003 | 1.002 | 1.002 | 866
Inner Dowsing Wind Farm Import | 1.003 | 1.003 | 1.002 | 1.002 | 867
Bicker Fen Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 868
London Road CHP (Import) | 1.02 | 1.02 | 1.019 | 1.019 | 869
Lindhurst Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 870
Staveley Works | 1.02 | 1.02 | 1.019 | 1.019 | 871
AP Drivelines | 1.02 | 1.02 | 1.019 | 1.019 | 872
Rolls Royce Coventry | 1.02 | 1.02 | 1.019 | 1.019 | 873
UK COAL MINING LTD | 1.02 | 1.02 | 1.019 | 1.019 | 874
Caterpillar | 1.02 | 1.02 | 1.019 | 1.019 | 875
Santander Carlton Park | 1.02 | 1.02 | 1.019 | 1.019 | 876
Brush | 1.02 | 1.02 | 1.019 | 1.019 | 877
JCB | 1.02 | 1.02 | 1.019 | 1.019 | 878
Cast Bar UK | 1.02 | 1.02 | 1.019 | 1.019 | 879
Bretby GP | 1.02 | 1.02 | 1.019 | 1.019 | 880
Holwell Works | 1.02 | 1.02 | 1.019 | 1.019 | 881
Pedigree Petfoods | 1.02 | 1.02 | 1.019 | 1.019 | 882
Alstom Wolverton | 1.02 | 1.02 | 1.019 | 1.019 | 883
Colworth Laboratory | 1.02 | 1.02 | 1.019 | 1.019 | 884
Boots Thane Road | 1.02 | 1.02 | 1.019 | 1.019 | 885
QMC | 1.02 | 1.02 | 1.019 | 1.019 | 886
British Gypsum | 1.02 | 1.02 | 1.019 | 1.019 | 887
Melbourne STW | 1.02 | 1.02 | 1.019 | 1.019 | 888
Whetstone | 1.02 | 1.02 | 1.019 | 1.019 | 889
Holbrook Works | 1.02 | 1.02 | 1.019 | 1.019 | 890
Astrazeneca Charnwood | 1.02 | 1.02 | 1.019 | 1.019 | 891
B&Q Manton (Import) | 1.02 | 1.02 | 1.019 | 1.019 | 892
Transco Churchover | 1.02 | 1.02 | 1.019 | 1.019 | 893
Alstom Rugby | 1.02 | 1.02 | 1.019 | 1.019 | 894
VSB Avenue | 1.014 | 1.014 | 1.012 | 1.013 | 895
Low Spinney Wind Farm | 1.014 | 1.014 | 1.012 | 1.013 | 896
SWINFORD WINDFARM (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 897
Yelvertoft Wind Farm | 1.014 | 1.014 | 1.012 | 1.013 | 898
Maxwell House Data Centre | 1.014 | 1.014 | 1.012 | 1.013 | 899
Burton Wolds Ext North Import | 1.014 | 1.014 | 1.012 | 1.013 | 902
Shacks Barn PV Import | 1.014 | 1.014 | 1.012 | 1.013 | 903
Hatton Gas Compressor | 1.015 | 1.015 | 1.014 | 1.013 | 904
North Hykeham EFW | 1.014 | 1.014 | 1.012 | 1.013 | 905
Sleaford Renewable (Import) | 1.003 | 1.003 | 1.002 | 1.044 | 906
Bilsthorpe Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 907
Old Dalby Lodge WndFarm Import | 1.014 | 1.014 | 1.012 | 1.013 | 908
Willoughby STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 909
Rolls Royce AB&E 33kV (Import) | 1.018 | 1.018 | 1.018 | 1.018 | 910
The Grange Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 911
Clay Lake STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 912
Balderton STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 913
Wymeswold Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 914
French Farm Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 915
Lilbourne Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 916
Chelvaston Renewable (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 917
Beachampton Solar Farm Import | 1.014 | 1.014 | 1.012 | 1.013 | 918
Croft End Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 919
M1 Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 920
Leamington STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 921
Low Farm Anaerobic Dig (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 922
Turweston Airfield Solar (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 923
Burton Pedwardine Solar (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 924
Little Morton Farm Solar (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 925
Rockingham | 1.02 | 1.02 | 1.019 | 1.019 | 930
Santander Carlton Park 132/11 | 1.005 | 1.005 | 1.005 | 1.005 | 931
Delphi Diesel | 1.02 | 1.02 | 1.019 | 1.019 | 932
Univ of Warwick (do not use) | 1.02 | 1.02 | 1.019 | 1.019 | 933
Lodge Farm Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 940
Ermine Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 941
Ridge Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 942
Winwick Wind Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 943
Watford Lodge Wind Farm (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 944
Leverton Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 945
Burton Pedwardine Phase 2 Imp | 1.014 | 1.014 | 1.012 | 1.013 | 946
Hartwell Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 947
Eakley Lanes Solar North (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 948
Eakley Lanes Solar South (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 949
Welbeck Colliery PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 950
Newton Road PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 951
New Albion WF (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 952
Moat Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 953
Bilsthorpe Solar (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 954
Hall Farm PV (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 955
Gaultney Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 956
Fiskerton Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 957
Mount Mill Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 958
Podington Airfield WF (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 959
Branston South PV Farm(Import) | 1.014 | 1.014 | 1.012 | 1.013 | 960
Eakring Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 961
Ragdale PV Solar Park (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 962
Thoresby Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 963
Welbeck Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 964
Atherstone Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 965
Babworth Estate PV Farm (Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 966
Gawcott Fields PV Boundary Imp | 1.014 | 1.014 | 1.012 | 1.013 | 967
Homestead Farm Solar Park(Imp) | 1.014 | 1.014 | 1.012 | 1.013 | 968
Grange Solar Farm (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 969
Grendon | 1.003 | 1.003 | 1.01 | 1.01 | 2034
East Claydon | 1.003 | 1.003 | 1.002 | 1.002 | 2227
Glutton Bridge | 1.036 | 1.034 | 1.027 | 1.03 | 2820
West Burton Power Station | 1 | 1 | 1 | 1 | 4010
Ratcliffe-on-Soar Power Station | 1 | 1 | 1 | 1 | 5016
Corby Power | 1.008 | 1.009 | 1.01 | 1.01 | 7015
Derwent Cogeneration | 1.003 | 1.003 | 1.002 | 1.002 | 7043
Redfield Road 1 STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 7315
Redfield Road B STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 7326
Trafalgar Pk Gas STOR (Import) | 1.014 | 1.014 | 1.012 | 1.013 | 7324
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Yew Tree Farm PV (Export) | 1.014 | 1.052 | 1.012 | 1.051 | 367
Cobb Farm Egmanton PV (Export) | 1.014 | 1.067 | 1.012 | 1.063 | 368
Kelmarsh Wind Farm (Export) | 1.012 | 1.012 | 1.012 | 1.012 | 369
PebHall_Welland_Waste_Export | 1.014 | 1.014 | 1.012 | 1.013 | 370
Copley Farm PV Claypole (Exp) | 1.023 | 1.019 | 1.023 | 1.018 | 371
Greatmoor EFW Calvert (Export) | 0.988 | 0.988 | 0.988 | 0.989 | 372
Lodge Farm (Calow) PV Export | 1.014 | 1.005 | 1.012 | 1.005 | 373
Arkwright Solar PV (Export) | 1.014 | 1.009 | 1.012 | 1.008 | 374
Langar Commercial PV (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 375
Redfield Road 1 STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 376
Averill Farm PV (Export) | 1.014 | 1.014 | 1.012 | 1.014 | 377
Marchington Solar PV (Export) | 1.014 | 1.027 | 1.012 | 1.026 | 378
West End Fm Treswell PV (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 379
Fields Farm Southam PV (Exp) | 1.014 | 1.029 | 1.012 | 1.029 | 380
Canopus Farm PV (Export) | 1.014 | 1.033 | 1.012 | 1.032 | 381
Lindridge Farm PV (Export) | 1.014 | 1.041 | 1.012 | 1.04 | 382
Thornborough Grnds PV (Export) | 1.014 | 1.03 | 1.012 | 1.03 | 383
Wymeswold Narrow Lane PV (Exp) | 1.014 | 1.016 | 1.012 | 1.016 | 384
Manor Farm Horton PV (Export) | 1.014 | 1.012 | 1.012 | 1.012 | 385
Handley Park Farm PV (Export) | 1.014 | 1.03 | 1.012 | 1.03 | 386
Shelton Lodge PV (Export) | 1.014 | 1.045 | 1.012 | 1.044 | 387
Brafield on the Green PV (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 388
Sywell PV (Export) | 1.014 | 1.004 | 1.012 | 1.004 | 389
Holtwood Farm PV (Export) | 1.014 | 1.025 | 1.012 | 1.025 | 390
Drakelow Farm PV (Export) | 1.014 | 1.003 | 1.012 | 1.003 | 391
Stragglethorpe Rd PV (Export) | 1.014 | 1.089 | 1.012 | 1.088 | 392
Oxcroft Solar Farm PV (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 393
Derby Waste Sinfin EFW (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 394
Littlewood Farm PV (Export) | 1.014 | 1.029 | 1.012 | 1.029 | 395
Twin Yards Farm PV (Export) | 1.014 | 1.027 | 1.012 | 1.027 | 396
Tower Hayes Farm PV (Export) | 1.014 | 1.025 | 1.012 | 1.025 | 397
The Breck Solar PV (Export) | 1.014 | 1.01 | 1.012 | 1.01 | 398
Barnby Moor Retford PV(Export) | 1.014 | 1.022 | 1.012 | 1.021 | 399
Lincoln Farm PV (Export) | 1.014 | 1.027 | 1.012 | 1.026 | 400
Drakelow Renewable BIO (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 401
Tetron Point ESS (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 402
Mill Fm Gt Ponton PV (Export) | 1.014 | 1.035 | 1.012 | 1.034 | 403
(PHF) Welland Bio Power Exp | 1.014 | 1.014 | 1.012 | 1.013 | 404
Deepdale Solar Fm PV (Export) | 1.014 | 1.029 | 1.012 | 1.029 | 405
Burton Wolds South WF (Export) | 0.959 | 0.958 | 0.961 | 0.961 | 406
Brafield_PV_Commercial (Exps) | 1.014 | 1.014 | 1.012 | 1.013 | 407
Brafield_PV_Community (Exps) | 1.014 | 1.014 | 1.012 | 1.013 | 408
Gawcott Flds PV Commercial Exp | 1.014 | 1.014 | 1.012 | 1.013 | 409
Gawcott Flds PV Community Exp | 1.014 | 1.014 | 1.012 | 1.013 | 410
Trafalgar Pk Gas STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 411
John Brookes Sawmill BIO (Exp) | 1.014 | 1.014 | 1.015 | 1.015 | 412
Hawton Wind Farm WF (Export) | 1.008 | 1.008 | 1.009 | 1.009 | 413
Blackbridge Farm BIO (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 414
Garnham Close STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 415
Bombardier (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 416
Langar Community PV (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 417
Hermitage Lane STOR (Export) | 1.022 | 1.025 | 1.026 | 1.025 | 418
Fosse Way Radford Sem PV (Exp) | 1.014 | 1.035 | 1.012 | 1.035 | 419
Meadow Fm Thorpe Lang PV (Exp) | 1.014 | 1.014 | 1.012 | 1.014 | 420
Olney Hyde Farm PV (Export) | 1.014 | 1.01 | 1.012 | 1.01 | 421
Dayfields Farm PV (Export) | 1.014 | 1.079 | 1.012 | 1.078 | 422
Bolsovermoor Quarry PV(Export) | 1.014 | 1.008 | 1.012 | 1.008 | 423
Bilsthorpe PV (Export) | 1.014 | 1.021 | 1.012 | 1.02 | 424
Carlton Forest STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 425
Sutton Bonnington PV (Export) | 1.014 | 1.042 | 1.012 | 1.042 | 426
Alfreton Diesel Power (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 427
Green Lane Marchington PV(Exp) | 1.014 | 1.026 | 1.012 | 1.025 | 428
Baddesley Park PV (Export) | 1.014 | 1.033 | 1.012 | 1.033 | 429
Baddesley Pk Biomass (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 430
Taylor Lane 33kV STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 431
Hill Farm ESS (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 432
Leverton ESS (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 433
Nottingham Rd STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 434
RAF Cranwell High G (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 435
Breach Farm ESS (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 436
Boston Biomass Gen AD (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 437
Twin Oaks Diesel STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 438
Colwick Private Rd STOR (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 439
Mill Fm Caythorpe ESS (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 440
(PHF) Welland Waste Exp | 1.014 | 1.014 | 1.012 | 1.013 | 441
Rhodia STOR (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 442
Lyon Road Gas Gen (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 479
Asher Lane 33kV STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 480
Spondon Peaking STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 481
Railtrack Bytham (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 600
Railtrack Grantham (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 601
Railtrack Staythorpe (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 602
Railtrack Retford (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 603
Railtrack Rugby (Export) | 1.015 | 1.015 | 1.012 | 1.015 | 604
Railtrack Tamworth (Export) | 1.01 | 1.01 | 1.012 | 1.01 | 605
Railtrack Wolverton (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 606
Acordis (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 607
QMC (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 608
ABR Foods (Export) | 1.011 | 1.011 | 1.011 | 1.011 | 609
Derby Co-Generation (Export) | 0.997 | 0.999 | 1.002 | 0.999 | 610
Bentinck (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 611
Calvert Landfill (Export) | 1.026 | 1.026 | 1.026 | 1.026 | 612
Weldon Landfill (Export) | 1.012 | 1.012 | 1.012 | 1.012 | 613
Goosy Lodge Power (Export) | 0.998 | 0.998 | 0.997 | 0.997 | 614
Burton Wolds Wind Farm Export | 1.007 | 1.007 | 1.008 | 1.007 | 615
Railtrack Bretton (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 616
Bambers Farm Wind Farm Export | 1.09 | 1.09 | 1.091 | 1.091 | 617
Vine House Wind Farm Export | 1.038 | 1.038 | 1.039 | 1.038 | 618
Red House Wind Farm Export | 1.067 | 1.067 | 1.068 | 1.068 | 619
Daneshill Landfill (Export) | 1.042 | 1.042 | 1.042 | 1.042 | 620
Newton Longville Export | 1.024 | 1.024 | 1.024 | 1.024 | 621
Hollies Wind Farm Export | 1.025 | 1.025 | 1.025 | 1.025 | 622
Lynn Wind Farm (Export) | 1.014 | 1.013 | 1.013 | 1.013 | 629
Inner Dowsing Wind Farm Export | 1.012 | 1.012 | 1.013 | 1.013 | 630
Bicker Fen Wind Farm (Export) | 1.029 | 1.029 | 1.031 | 1.03 | 631
Cov & Sol Waste (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 632
Lindhurst Wind Farm (Export) | 1.028 | 1.028 | 1.029 | 1.029 | 633
London Road CHP (Export) | 1.019 | 1.019 | 1.019 | 1.019 | 634
Petsoe Wind Farm (Export) | 1.032 | 1.032 | 1.033 | 1.033 | 635
Boots Thane Road (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 636
B&Q Manton (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 637
Low Spinney Wind Farm (Export) | 1.034 | 1.034 | 1.034 | 1.035 | 638
SWINFORD WINDFARM (Export) | 1.026 | 1.025 | 1.026 | 1.026 | 639
Asfordby Generation | 0.999 | 1 | 1.002 | 1.002 | 640
Yelvertoft (Export) | 1.04 | 1.04 | 1.041 | 1.041 | 641
North Hykeham Export | 1.039 | 1.039 | 1.039 | 1.039 | 642
Sleaford Renewable (Export) | 1.029 | 1.029 | 1.03 | 1.031 | 643
Bilsthorpe Wind Farm (Export) | 1.033 | 1.033 | 1.034 | 1.034 | 644
Old Dalby Lodge WndFarm Export | 1.016 | 1.016 | 1.016 | 1.016 | 645
Lilbourne Wind Farm (Export) | 1.032 | 1.032 | 1.033 | 1.032 | 646
The Grange Wind Farm (Export) | 1.041 | 1.041 | 1.042 | 1.042 | 647
Clay Lake STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 648
Balderton STOR (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 649
Burton Wolds Ext North Export | 1.001 | 1.002 | 1.002 | 1.002 | 650
Shacks Barn PV Export | 1.014 | 1.027 | 1.012 | 1.027 | 651
Willoughby STOR (Export) | 1.015 | 1.015 | 1.012 | 1.015 | 652
Wymeswold Solar Park (Export) | 1.026 | 1.024 | 1.026 | 1.024 | 653
French Farm Wind Farm (Export) | 1.046 | 1.046 | 1.047 | 1.046 | 654
Chelvaston Renewable (Export) | 1 | 0.999 | 1.001 | 0.997 | 655
Beachampton Solar Farm Export | 1.014 | 1.018 | 1.012 | 1.018 | 656
Croft End Solar Farm (Export) | 1.014 | 1.025 | 1.012 | 1.025 | 657
M1 Wind Farm (Export) | 1.013 | 1.013 | 1.013 | 1.013 | 658
Leamington STOR Export | 1.014 | 1.014 | 1.012 | 1.013 | 659
Low Farm Anaerobic Dig (Exp) | 1.04 | 1.04 | 1.041 | 1.041 | 660
Welbeck Colliery PV ( Export) | 1.014 | 1.028 | 1.012 | 1.026 | 661
Newton Road PV (Export) | 1.014 | 1.01 | 1.012 | 1.009 | 662
New Albion WF (Export) | 1.007 | 1.007 | 1.008 | 1.008 | 663
Moat Farm PV (Export) | 1.014 | 1.039 | 1.012 | 1.039 | 664
Bilsthorpe Solar (Export) | 1.014 | 1.046 | 1.012 | 1.044 | 665
Hall Farm PV (Export) | 1.014 | 1.039 | 1.012 | 1.038 | 666
Gaultney Solar Park (Export) | 1.014 | 1.01 | 1.012 | 1.01 | 667
Fiskerton Solar Farm (Export) | 1.014 | 1.04 | 1.012 | 1.039 | 668
Mount Mill Solar Park (Export) | 1.014 | 1.017 | 1.012 | 1.017 | 669
Podington Airfield WF (Export) | 1.001 | 1.001 | 1.002 | 1.002 | 670
Branston South PV Farm(Export) | 1.014 | 1.047 | 1.05 | 1.044 | 671
Eakring Solar Farm (Export) | 1.014 | 1.023 | 1.012 | 1.022 | 672
Ragdale PV Solar Park (Export) | 1.014 | 1.027 | 1.012 | 1.025 | 673
Thoresby Solar Farm (Export) | 1.014 | 1.041 | 1.044 | 1.039 | 674
Welbeck Solar Farm (Export) | 1.014 | 1.03 | 1.012 | 1.029 | 675
Atherstone Solar Farm (Export) | 1.014 | 1.048 | 1.012 | 1.046 | 676
Babworth Estate PV Farm (Exp) | 1.014 | 1.041 | 1.012 | 1.04 | 677
Gawcott Fields PV Boundary Exp | 1.014 | 1.014 | 1.012 | 1.013 | 678
Homestead Farm Solar Park(Exp) | 1.014 | 1.026 | 1.028 | 1.025 | 679
Grange Solar Farm (Export) | 1.014 | 1.099 | 1.012 | 1.096 | 680
University of Warwick (Export) | 1.02 | 1.02 | 1.019 | 1.019 | 684
Turweston Airfield Solar (Exp) | 1.014 | 1.018 | 1.012 | 1.018 | 691
Burton Pedwardine Solar (Exp) | 1.014 | 1.026 | 1.012 | 1.026 | 692
Little Morton Farm Solar (Exp) | 1.014 | 1.033 | 1.012 | 1.033 | 693
Lodge Farm Solar Park (Export) | 1.014 | 1.043 | 1.012 | 1.041 | 694
Ermine Farm PV (Export) | 1.023 | 1.021 | 1.023 | 1.02 | 695
Ridge Solar Park (Export) | 1.014 | 1.003 | 1.012 | 1.003 | 696
Winwick Wind Farm (Export) | 1.027 | 1.026 | 1.028 | 1.029 | 697
Watford Lodge Wind Farm (Exp) | 1.028 | 1.028 | 1.029 | 1.029 | 698
Leverton Solar Park (Export) | 1.014 | 1.036 | 1.012 | 1.035 | 699
Castle Cement (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 700
Burton Pedwardine Phase 2 Exp | 1.014 | 1.026 | 1.012 | 1.026 | 701
Hartwell Solar Farm (Export) | 1.014 | 1.012 | 1.012 | 1.009 | 702
Eakley Lanes Solar North (Exp) | 1.014 | 1.011 | 1.012 | 1.011 | 703
Eakley Lanes Solar South (Exp) | 1.012 | 1.011 | 1.012 | 1.011 | 704
Prestop Park Farm PV (Export) | 1.014 | 1.029 | 1.012 | 1.03 | 705
Smith Hall Farm Solar (Export) | 1.014 | 1.06 | 1.012 | 1.059 | 706
Park Farm Solar Ashby (Export) | 1.014 | 1.024 | 1.012 | 1.022 | 707
Aston House Solar Farm(Export) | 1.014 | 1.014 | 1.012 | 1.012 | 708
Normanton-le-Heath PV Fm (Exp) | 1.014 | 1.014 | 1.012 | 1.013 | 709
Elms Farm Solar Farm (Export) | 1.014 | 1.026 | 1.012 | 1.025 | 710
Morton Solar Farm (Export) | 1.014 | 1.033 | 1.034 | 1.032 | 711
Glebe Farm Podington PV-Export | 0.999 | 0.997 | 0.999 | 0.997 | 712
Rolleston Park Solar (Export) | 1.014 | 1.012 | 1.012 | 1.012 | 713
Nowhere Farm PV (Export) | 1.014 | 1.039 | 1.012 | 1.038 | 714
Lockington Solar Farm (Export) | 1.014 | 1.014 | 1.012 | 1.013 | 715
Chelveston Renewable PV-Export | 1.014 | 1.004 | 1.005 | 1.003 | 716
Horsemoor Drove Solar (Export) | 1.014 | 1.037 | 1.012 | 1.037 | 717
Decoy Farm Crowland PV-Export | 1.014 | 1.051 | 1.012 | 1.05 | 718
Decoy Farm Crowland Bio-Export | 1.014 | 1.014 | 1.012 | 1.013 | 719
Decoy Farm Crowland AD-Export | 1.049 | 1.05 | 1.05 | 1.05 | 720
Redfield Road 1 STOR (Export) | 1.013 | 1.015 | 1.012 | 1.015 | 7316
Redfield Road B STOR (Export) | 1.011 | 1.015 | 1.015 | 1.014 | 7327
Trafalgar Pk Gas STOR (Export) | 1.016 | 1.018 | 1.012 | 1.018 | 7325

## NORW - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
Electricity North West - Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October |  |  | 00:00 - 07:00 | 07:00 - 00:00
Monday to Friday November to February | 16:00 – 19:00 | 07:00 – 16:00 19:00 – 00:00 | 00:00 - 07:00
Saturday and Sunday All Year |  |  | 00:00 - 07:00 | 07:00 - 00:00
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network | 1.093 | 1.085 | 1.073 | 1.079 | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation | 1.048 | 1.047 | 1.047 | 1.045 | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network | 1.035 | 1.032 | 1.027 | 1.03 | 483, 753, 803, 973, 983, 843
High-voltage substation | 1.024 | 1.023 | 1.021 | 1.022 | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV | 1.019 | 1.018 | 1.015 | 1.017
EHV 132 kV to 33 kV | 1.013 | 1.013 | 1.011 | 1.012
EHV 132 kV | 1.009 | 1.008 | 1.006 | 1.007
| 1.078 | 1.073 | 1.065 | 1.067
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## SEPD - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
SEPD - Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## SHEPD - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
SHEPD - Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## MANWEB - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
Manweb- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## SPD - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
SPD- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## LPN - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
SPD- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## SPN - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
SPN- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## EPN - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
EPN- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350

## NPG Y - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
NPG Yorkshire- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4
| Winter Peak | Winter Daytime | Night | Other
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Low-voltage network |  |  |  |  | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation |  |  |  |  | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network |  |  |  |  | 483, 753, 803, 973, 983, 843
High-voltage substation |  |  |  |  | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4
Site 1 | 1.032 | 1.032 | 1.032 | 1.032
Site 2 | 1.002 | 1.002 | 1.002 | 1.002
Site 3 | 1.012 | 1.012 | 1.012 | 1.012
Site 4 | 1.053 | 1.053 | 1.053 | 1.053
Site 5 | 1.024 | 1.024 | 1.024 | 1.024
Site 6 | 1.015 | 1.015 | 1.015 | 1.015
Site 7 | 1.035 | 1.035 | 1.035 | 1.035
Site 8 | 1.003 | 1.003 | 1.003 | 1.003
Site 9 | 1.005 | 1.005 | 1.005 | 1.005
Site 10 | 1.019 | 1.019 | 1.019 | 1.019
Site 11 | 1.014 | 1.014 | 1.014 | 1.014
Site 12 | 1 | 1 | 1 | 1
Site 13 | 0.999 | 0.999 | 0.999 | 0.999
Site 14 | 1.007 | 1.007 | 1.007 | 1.007
Site 15 | 1.073 | 1.073 | 1.073 | 1.073
Site 16 | 1.013 | 1.013 | 1.013 | 1.013
Site 17 | 1.019 | 1.019 | 1.019 | 1.019
Site 18 | 1.077 | 1.077 | 1.077 | 1.077
Site 19 | 1.008 | 1.008 | 1.008 | 1.008
Site 20 | 1.011 | 1.011 | 1.011 | 1.011
Site 21 | 1 | 1 | 1 | 1
Site 22 | 1 | 1 | 1 | 1
Site 23 | 1 | 1 | 1 | 1
Site 24 | 1 | 1 | 1 | 1
Site 25 | 1 | 1 | 1 | 1
Site 26 | 1 | 1 | 1 | 1
Site 27 | 1 | 1 | 1 | 1
Site 28 | 1 | 1 | 1 | 1
Site 29 | 1 | 1 | 1 | 1
Site 30 | 1 | 1 | 1 | 1
Site 31 | 1.005 | 1.005 | 1.005 | 1.005
Site 32 | 1 | 1 | 1 | 1
Site 33 | 1 | 1 | 1 | 1
Site 34 | 1 | 1 | 1 | 1
Site 35 | 1.008 | 1.008 | 1.008 | 1.008
Site 36 | 1.01 | 1.01 | 1.01 | 1.01
Site 37 | 1 | 1 | 1 | 1
Site 68 | 1 | 1 | 1 | 1
Site 69 | 1 | 1 | 1 | 1
Site 70 | 1 | 1 | 1 | 1
Site 71 | 1 | 1 | 1 | 1
Site 72 | 1 | 1 | 1 | 1
Site 73 | 1 | 1 | 1 | 1
Site 74 | 1 | 1 | 1 | 1
Site 75 | 1 | 1 | 1 | 1
Site 76 | 1 | 1 | 1 | 1
Site 77 | 1 | 1 | 1 | 1
Site 78 | 1 | 1 | 1 | 1
Site 79 | 1 | 1 | 1 | 1
Site 80 | 1 | 1 | 1 | 1
Site 81 | 1 | 1 | 1 | 1
Site 82 | 1 | 1 | 1 | 1
Site 84 | 0.99 | 0.99 | 0.99 | 0.99
Site 85 | 0.999 | 0.999 | 0.999 | 0.999
Site 90 | 1.011 | 1.011 | 1.011 | 1.011
Site 91 | 0.995 | 0.995 | 0.995 | 0.995
Site 92 | 1.009 | 1.009 | 1.009 | 1.009
Site 95 | 1 | 1 | 1 | 1
Site 96 | 1 | 1 | 1 | 1
Site 97 | 1 | 1 | 1 | 1
Site 98 | 1.006 | 1.006 | 1.006 | 1.006
Site 99 | 1.006 | 1.006 | 1.006 | 1.006
Site 100 | 1.013 | 1.013 | 1.013 | 1.013
Site 101 | 1.002 | 1.002 | 1.002 | 1.002
Site 102 | 1 | 1 | 1 | 1
Site 103 | 1 | 1 | 1 | 1
Site 104 | 1 | 1 | 1 | 1
Site 107 | 1 | 1 | 1 | 1
Site 110 | 1.004 | 1.004 | 1.004 | 1.004
Site 111 | 1 | 1 | 1 | 1
tbc | 0.994 | 0.994 | 0.994 | 0.994
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4
Site 8 | 1 | 1 | 1 | 1
Site 12 | 1 | 1 | 1 | 1
Site 13 | 0.99 | 0.99 | 0.99 | 0.99
Site 14 | 1 | 1 | 1 | 1
Site 15 | 1 | 1 | 1 | 1
Site 16 | 0.999 | 0.999 | 0.999 | 0.999
Site 17 | 1.001 | 1.001 | 1.001 | 1.001
Site 18 | 1.001 | 1.001 | 1.001 | 1.001
Site 19 | 1.001 | 1.001 | 1.001 | 1.001
Site 20 | 1 | 1 | 1 | 1
Site 21 | 0.995 | 0.995 | 0.995 | 0.995
Site 22 | 0.992 | 0.992 | 0.992 | 0.992
Site 23 | 0.994 | 0.994 | 0.994 | 0.994
Site 24 | 0.992 | 0.992 | 0.992 | 0.992
Site 25 | 0.977 | 0.977 | 0.977 | 0.977
Site 26 | 0.993 | 0.993 | 0.993 | 0.993
Site 27 | 0.999 | 0.999 | 0.999 | 0.999
Site 28 | 0.998 | 0.998 | 0.998 | 0.998
Site 29 | 0.989 | 0.989 | 0.989 | 0.989
Site 30 | 0.994 | 0.994 | 0.994 | 0.994
Site 31 | 0.999 | 0.999 | 0.999 | 0.999
Site 32 | 1 | 1 | 1 | 1
Site 33 | 0.991 | 0.991 | 0.991 | 0.991
Site 34 | 1.01 | 1.01 | 1.01 | 1.01
Site 68 | 1.002 | 1.002 | 1.002 | 1.002
Site 69 | 1.013 | 1.013 | 1.013 | 1.013
Site 70 | 0.982 | 0.982 | 0.982 | 0.982
Site 71 | 1.012 | 1.012 | 1.012 | 1.012
Site 72 | 0.996 | 0.996 | 0.996 | 0.996
Site 73 | 0.996 | 0.996 | 0.996 | 0.996
Site 74 | 0.992 | 0.992 | 0.992 | 0.992
Site 75 | 1 | 1 | 1 | 1
Site 76 | 0.983 | 0.983 | 0.983 | 0.983
Site 77 | 0.994 | 0.994 | 0.994 | 0.994
Site 78 | 0.999 | 0.999 | 0.999 | 0.999
Site 79 | 0.991 | 0.991 | 0.991 | 0.991
Site 80 | 0.998 | 0.998 | 0.998 | 0.998
Site 81 | 0.994 | 0.994 | 0.994 | 0.994
Site 82 | 0.992 | 0.992 | 0.992 | 0.992
Site 84 | 0.99 | 0.99 | 0.99 | 0.99
Site 85 | 0.999 | 0.999 | 0.999 | 0.999
Site 90 | 1.011 | 1.011 | 1.011 | 1.011
Site 91 | 0.995 | 0.995 | 0.995 | 0.995
Site 92 | 1.009 | 1.009 | 1.009 | 1.009
Site 95 | 0.998 | 0.998 | 0.998 | 0.998
Site 96 | 0.998 | 0.998 | 0.998 | 0.998
Site 97 | 0.997 | 0.997 | 0.997 | 0.997
Site 98 | 0.909 | 0.909 | 0.909 | 0.909
Site 99 | 0.909 | 0.909 | 0.909 | 0.909
Site 100 | 0.987 | 0.987 | 0.987 | 0.987
Site 102 | 0.996 | 0.996 | 0.996 | 0.996
Site 103 | 0.996 | 0.996 | 0.996 | 0.996
Site 104 | 0.997 | 0.997 | 0.997 | 0.997
Site 107 | 0.998 | 0.998 | 0.998 | 0.998
Site 110 | 0.993 | 0.993 | 0.993 | 0.993
Site 111 | 0.99 | 0.99 | 0.99 | 0.99
tbc | 1 | 1 | 1 | 1
tbc | 0.999 | 0.999 | 0.999 | 0.999
tbc | 0.994 | 0.994 | 0.994 | 0.994

## NPG NE - Annex 5 LLFs
These line loss factors are illustrative based on the latest calculated values and are published in good faith. However, the line loss factors that are approved by the BSC Panel for the applicable year and consequently published on the Elexon website will take precedence and be used in Settlement if they differ from these values.
NPG North East- Final LLFs for year beginning 1 April 2019
Time periods | Period 1 | Period 2 | Period 3 | Period 4 | Period 5
| Winter Peak | Winter Daytime | Night | Other | Extra
Monday to Friday March to October
Monday to Friday November to February
Saturday and Sunday All Year
Notes | All the above times are in UK Clock time
Generic demand and generation LLFs
Metered voltage, respective periods and associated LLFCs
Metered voltage | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Associated LLFC
Low-voltage network | [5 empty] | 11, 31, 41, 51, 61, 81, 91, 131, 161, 171, 191, 241, 431, 441, 451, 481, 511, 531, 581, 591, 631, 661, 751, 761, 771, 781, 791, 801, 811, 821, 831, 961, 971, 981, 851, 861, 841, 901
Low-voltage substation | [5 empty] | 242, 432, 482, 752, 802, 962, 972, 982, 842
High-voltage network | [5 empty] | 483, 753, 803, 973, 983, 843
High-voltage substation | [5 empty] | 109, 119, 129, 139, 149, 159, 169, 179, 189, 199, 209, 219, 229, 239, 249, 259, 269, 289, 299, 309, 319, 329, 339, 349, 359, 369, 379, 389, 419, 439, 459, 469, 529, 539, 549, 579, 599, 619, 639, 659, 679, 699, 719, 739, 759, 779, 799, 479, 489, 499, 509, 519, 589, 609, 629, 649, 669, 689, 709, 729, 749, 769, 789, 809
EHV 33 kV
EHV 132 kV to 33 kV
EHV 132 kV
EHV site specific LLFs
Demand
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 1 | 1.032 | 1.032 | 1.032 | 1.032 | 610
Site 2 | 1.002 | 1.002 | 1.002 | 1.002 | 500
Site 3 | 1.012 | 1.012 | 1.012 | 1.012 | 650
Site 4 | 1.053 | 1.053 | 1.053 | 1.053 | 660
Site 5 | 1.024 | 1.024 | 1.024 | 1.024 | 640
Site 6 | 1.015 | 1.015 | 1.015 | 1.015 | 700
Site 7 | 1.035 | 1.035 | 1.035 | 1.035 | 900
Site 8 | 1.003 | 1.003 | 1.003 | 1.003 | 670
Site 9 | 1.005 | 1.005 | 1.005 | 1.005 | 320
Site 10 | 1.019 | 1.019 | 1.019 | 1.019 | 850
Site 11 | 1.014 | 1.014 | 1.014 | 1.014 | 450
Site 12 | 1 | 1 | 1 | 1 | 460
Site 13 | 0.999 | 0.999 | 0.999 | 0.999 | 680
Site 14 | 1.007 | 1.007 | 1.007 | 1.007 | 520
Site 15 | 1.073 | 1.073 | 1.073 | 1.073 | 510
Site 16 | 1.013 | 1.013 | 1.013 | 1.013 | 530
Site 17 | 1.019 | 1.019 | 1.019 | 1.019 | 540
Site 18 | 1.077 | 1.077 | 1.077 | 1.077 | 550
Site 19 | 1.008 | 1.008 | 1.008 | 1.008 | 810
Site 20 | 1.011 | 1.011 | 1.011 | 1.011 | 830
Site 21 | 1 | 1 | 1 | 1 | 960
Site 22 | 1 | 1 | 1 | 1 | 370
Site 23 | 1 | 1 | 1 | 1 | 410
Site 24 | 1 | 1 | 1 | 1 | 430
Site 25 | 1 | 1 | 1 | 1 | 340
Site 26 | 1 | 1 | 1 | 1 | 480
Site 27 | 1 | 1 | 1 | 1 | 600
Site 28 | 1 | 1 | 1 | 1 | 980
Site 29 | 1 | 1 | 1 | 1 | 280
Site 30 | 1 | 1 | 1 | 1 | 260
Site 31 | 1.005 | 1.005 | 1.005 | 1.005 | 180
Site 32 | 1 | 1 | 1 | 1 | 200
Site 33 | 1 | 1 | 1 | 1 | 140
Site 34 | 1 | 1 | 1 | 1 | 160
Site 35 | 1.008 | 1.008 | 1.008 | 1.008 | 950
Site 36 | 1.01 | 1.01 | 1.01 | 1.01 | 910
Site 37 | 1 | 1 | 1 | 1 | 920
Site 68 | 1 | 1 | 1 | 1 | 110
Site 69 | 1 | 1 | 1 | 1 | 220
Site 70 | 1 | 1 | 1 | 1 | 80
Site 71 | 1 | 1 | 1 | 1 | 40
Site 72 | 1 | 1 | 1 | 1 | 60
Site 73 | 1 | 1 | 1 | 1 | 68
Site 74 | 1 | 1 | 1 | 1 | 20
Site 75 | 1 | 1 | 1 | 1 | 10
Site 76 | 1 | 1 | 1 | 1 | 88
Site 77 | 1 | 1 | 1 | 1 | 237
Site 78 | 1 | 1 | 1 | 1 | 257
Site 79 | 1 | 1 | 1 | 1 | 277
Site 80 | 1 | 1 | 1 | 1 | 297
Site 81 | 1 | 1 | 1 | 1 | 187
Site 82 | 1 | 1 | 1 | 1 | 207
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 1 | 1 | 1 | 1 | 307
Site 96 | 1 | 1 | 1 | 1 | 327
Site 97 | 1 | 1 | 1 | 1 | 347
Site 98 | 1.006 | 1.006 | 1.006 | 1.006 | 367
Site 99 | 1.006 | 1.006 | 1.006 | 1.006 | 387
Site 100 | 1.013 | 1.013 | 1.013 | 1.013 | 437
Site 101 | 1.002 | 1.002 | 1.002 | 1.002 | 457
Site 102 | 1 | 1 | 1 | 1 | 417
Site 103 | 1 | 1 | 1 | 1 | 467
Site 104 | 1 | 1 | 1 | 1 | 108
Site 107 | 1 | 1 | 1 | 1 | 128
Site 110 | 1.004 | 1.004 | 1.004 | 1.004 | 487
Site 111 | 1 | 1 | 1 | 1 | 517
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350
EHV site specific LLFs
Generation
Site | Period 1 | Period 2 | Period 3 | Period 4 | Associated LLFC
Site 8 | 1 | 1 | 1 | 1 | 217
Site 12 | 1 | 1 | 1 | 1 | 470
Site 13 | 0.99 | 0.99 | 0.99 | 0.99 | 690
Site 14 | 1 | 1 | 1 | 1 | 730
Site 15 | 1 | 1 | 1 | 1 | 720
Site 16 | 0.999 | 0.999 | 0.999 | 0.999 | 770
Site 17 | 1.001 | 1.001 | 1.001 | 1.001 | 740
Site 18 | 1.001 | 1.001 | 1.001 | 1.001 | 750
Site 19 | 1.001 | 1.001 | 1.001 | 1.001 | 820
Site 20 | 1 | 1 | 1 | 1 | 840
Site 21 | 0.995 | 0.995 | 0.995 | 0.995 | 970
Site 22 | 0.992 | 0.992 | 0.992 | 0.992 | 360
Site 23 | 0.994 | 0.994 | 0.994 | 0.994 | 420
Site 24 | 0.992 | 0.992 | 0.992 | 0.992 | 440
Site 25 | 0.977 | 0.977 | 0.977 | 0.977 | 350
Site 26 | 0.993 | 0.993 | 0.993 | 0.993 | 490
Site 27 | 0.999 | 0.999 | 0.999 | 0.999 | 590
Site 28 | 0.998 | 0.998 | 0.998 | 0.998 | 990
Site 29 | 0.989 | 0.989 | 0.989 | 0.989 | 290
Site 30 | 0.994 | 0.994 | 0.994 | 0.994 | 270
Site 31 | 0.999 | 0.999 | 0.999 | 0.999 | 190
Site 32 | 1 | 1 | 1 | 1 | 210
Site 33 | 0.991 | 0.991 | 0.991 | 0.991 | 150
Site 34 | 1.01 | 1.01 | 1.01 | 1.01 | 170
Site 68 | 1.002 | 1.002 | 1.002 | 1.002 | 120
Site 69 | 1.013 | 1.013 | 1.013 | 1.013 | 230
Site 70 | 0.982 | 0.982 | 0.982 | 0.982 | 90
Site 71 | 1.012 | 1.012 | 1.012 | 1.012 | 50
Site 72 | 0.996 | 0.996 | 0.996 | 0.996 | 70
Site 73 | 0.996 | 0.996 | 0.996 | 0.996 | 78
Site 74 | 0.992 | 0.992 | 0.992 | 0.992 | 30
Site 75 | 1 | 1 | 1 | 1 | 100
Site 76 | 0.983 | 0.983 | 0.983 | 0.983 | 98
Site 77 | 0.994 | 0.994 | 0.994 | 0.994 | 227
Site 78 | 0.999 | 0.999 | 0.999 | 0.999 | 247
Site 79 | 0.991 | 0.991 | 0.991 | 0.991 | 267
Site 80 | 0.998 | 0.998 | 0.998 | 0.998 | 287
Site 81 | 0.994 | 0.994 | 0.994 | 0.994 | 177
Site 82 | 0.992 | 0.992 | 0.992 | 0.992 | 197
Site 84 | 0.99 | 0.99 | 0.99 | 0.99 | MSID 7039 & 7040
Site 85 | 0.999 | 0.999 | 0.999 | 0.999 | MSID 7107
Site 90 | 1.011 | 1.011 | 1.011 | 1.011 | MSID 2037 & 2038
Site 91 | 0.995 | 0.995 | 0.995 | 0.995 | MSID 7156
Site 92 | 1.009 | 1.009 | 1.009 | 1.009 | MSID 0437
Site 95 | 0.998 | 0.998 | 0.998 | 0.998 | 317
Site 96 | 0.998 | 0.998 | 0.998 | 0.998 | 337
Site 97 | 0.997 | 0.997 | 0.997 | 0.997 | 357
Site 98 | 0.909 | 0.909 | 0.909 | 0.909 | 377
Site 99 | 0.909 | 0.909 | 0.909 | 0.909 | 397
Site 100 | 0.987 | 0.987 | 0.987 | 0.987 | 427
Site 102 | 0.996 | 0.996 | 0.996 | 0.996 | 407
Site 103 | 0.996 | 0.996 | 0.996 | 0.996 | 477
Site 104 | 0.997 | 0.997 | 0.997 | 0.997 | 118
Site 107 | 0.998 | 0.998 | 0.998 | 0.998 | 138
Site 110 | 0.993 | 0.993 | 0.993 | 0.993 | 497
Site 111 | 0.99 | 0.99 | 0.99 | 0.99 | 527
tbc | 1 | 1 | 1 | 1 | 710
tbc | 0.999 | 0.999 | 0.999 | 0.999 | 507
tbc | 0.994 | 0.994 | 0.994 | 0.994 | MSID 7350