Installation Document for Type A Power Generating Modules (Form A3-1) and Integrated Micro Generation and Storage (Form A3-2)

| Form A3-1 : Installation Document for Type A Power Generating Modules Please complete and provide this document for every Power Generating Facility. Part 1 should be completed for the Power Generating Facility. Part 2 should be completed for each of the Power Generating Modules being commissioned. Where the installation is phased the form should be completed on a per Generating Unit basis as each part of the installation is completed in accordance with EREC G99 paragraph 15.3.3. For phased installations reference to PGM in this form should be read as reference to Generating Units. |  |
| --- | --- |
| Form A3-1 Part 1 |  |
| To ABC electricity distribution DNO 99 West St, Imaginary Town, ZZ99 9AA abced@wxyz.com |  |
| Generator Details: |  |
| Generator (name) |  |
| Address |  |
| Post Code |  |
| Contact person (if different from Generator) |  |
| Telephone number |  |
| E-mail address |  |
| MPAN(s) |  |
| Generator signature |  |
| Installer Details: |  |
| Installer |  |
| Accreditation / Qualification |  |
| Address |  |

| Post Code |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Contact person |  |  |  |  |  |  |  |  |  |  |
| Telephone Number |  |  |  |  |  |  |  |  |  |  |
| E-mail address |  |  |  |  |  |  |  |  |  |  |
| Installer signature |  |  |  |  |  |  |  |  |  |  |
| Installation details |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |
| Post code |  |  |  |  |  |  |  |  |  |  |
| Location within Generator’s Installation |  |  |  |  |  |  |  |  |  |  |
| Location of Lockable Isolation Switch |  |  |  |  |  |  |  |  |  |  |
| Summary details of Power Generating Modules - where multiple Power Generating Modules will exist within one Generator’s Installation. |  |  |  |  |  |  |  |  |  |  |
| Manufacturer / Reference | Date of Installation |  | Technology Type | Manufacturers Ref No. (Product ID) or Reference to Form A2- 1/2/3 or combination of above as applicable | Power Generating Module Registered Capacity in kW |  |  |  |  |  |
|  |  |  |  |  | 3- Phase Units | Single Phase Units |  |  |  | Power Factor |
|  |  |  |  |  |  | PH 1 |  | PH 2 | PH 3 |  |
| Emerging technology classification (if applicable). |  |  |  |  |  |  |  |  |  |  |
| Commissioning Checks. |  |  |  |  |  |  |  |  |  |  |
| Description |  |  |  |  |  |  | Confirmation |  |  |  |
| Generator’s Installation satisfies the requirements of BS7671 (IET Wiring Regulations). |  |  |  |  |  |  | Yes / No* |  |  |  |

| Suitable lockable points of isolation have been provided between the PGMs and the rest of the Generator’s Installation. |  |  | Yes / No* |
| --- | --- | --- | --- |
| Labels have been installed at all points of isolation in accordance with EREC G99. |  |  | Yes / No* |
| Interlocking that prevents PGMs being connected in parallel with the DNO’s Distribution Network (without synchronising) is in place and operates correctly. |  |  | Yes / No* |
| Balance of Multiple Single Phase PGMs. Confirm that design of the Generator’s Installation has been carried out to limit output power imbalance to below 16 A per phase, as required by EREC G99. |  |  | Yes / No* |
| Form A3-1 Part 2 |  |  |  |
| Power Generating Module reference or name |  |  |  |
| Information to be enclosed. |  |  |  |
| Description |  | Confirmation * |  |
| Schedule of protection settings (may be included in circuit diagram) |  | Yes / No* |  |
| As installed Standard Application Form data, unless already provided. |  | Yes / No* |  |
| Final copy of circuit diagram |  | Yes / No* |  |
| Commissioning Checks. |  |  |  |
| The Interface Protection settings have been checked and comply with EREC G99. |  | Yes / No / N/A (Type Tested)* |  |
| The PGM successfully synchronises with the DNO’s Distribution Network without causing significant voltage disturbance. |  | Yes / No* |  |
| The PGM successfully runs in parallel with the DNO’s Distribution Network without tripping and without causing significant voltage disturbances. |  | Yes / No* |  |
| The PGM successfully disconnects without causing a significant voltage disturbance, when it is shut down. |  | Yes / No* |  |
| Interface Protection operates and disconnects the DNO’s Distribution Network quickly (within 1 s) when a suitably rated switch, located between the PGM and the DNO’s incoming connection, is opened. |  | Yes / No* |  |
| The PGM remains disconnected for at least 20 s after switch is reclosed. |  | Yes / No* |  |
| Loss of tripping and auxiliary supplies. Where applicable, loss of supplies to tripping and protection relays results in either PGM forced trip or an alarm to a 24 hour manned control centre. |  | Yes / No* |  |

| *Circle as appropriate. If “No” is selected the Power Generating Facility is deemed to have failed the commissioning tests and the Power Generating Module shall not be put in service. |  |
| --- | --- |
| Additional comments / observations: |  |
| Declaration – to be completed by Generator or Generator’s Appointed Technical Representative. |  |
| I declare that for the Type A Power Generating Module within the scope of this EREC G99, and the installation: - Compliance with the requirements of EREC G99 is achieved. - The commissioning checks detailed in Form A2-4 have been successfully completed*. - The commissioning checks detailed in this Form A3-1 have been successfully completed. *delete if not applicable ie if the Interface Protection and ride through capabilities are Type Tested. |  |
| Name: |  |
| Signature: | Date: |
| Company Name: |  |
| Position: |  |
| Declaration – to be completed by DNO Witnessing Representative if applicable. Delete if not witnessed by the DNO. |  |
| I confirm that I have witnessed: - The commissioning checks detailed in Form A2-4 *; - The commissioning checks detailed in this Form A3-1 on behalf of and that the results are an accurate record of the checks. *delete if not applicable ie if the Interface Protection and ride through capabilities are Type Tested |  |
| Name: |  |
| Signature: | Date: |
| Company Name: |  |