Completion Certificate – Service Jointing

Metered and Unmetered Electricity Service Installations

Section 1 – Checklist

|  | ICP |
| --- | --- |
| An as laid drawing(s) has been prepared and is attached to the form |  |
| The person undertaking the associated tests and completing this certificate is duly authorised within the Quality Management System |  |

Section 2 – Project Details

Electricity North West Reference Number:

ICP Reference Number:

| Location Details | ICP |
| --- | --- |
| Title: | Company name: |
|  | Contact name: |
| Details: | Contact telephone number: |
| Town / City: | Contact email: |

Section 3 – Completion Certificate

Pre-energisation – commissioning test results

Note – minimum IR to be > or = 100M  ohms at 500v

|  | Plot Number / Unmetered Street Furniture Reference |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LV Service continuity test (Y/N) |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance (M ohms) |  |  |  |  |  |  |  |  |  |  |

Post-energisation – commissioning test results

Note – maximum earth loop impedence for PME to be 0.35 ohms; for non PME 0.8 ohms

|  | Plot Number / Unmetered Street Furniture Reference |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Earth loop impedance (ohms) |  |  |  |  |  |  |  |  |  |  |
| Phase colour (L1, L2, L3) |  |  |  |  |  |  |  |  |  |  |
| Phase rotation check (Y, N or N/A) |  |  |  |  |  |  |  |  |  |  |
| Is polarity correct (Y/N) |  |  |  |  |  |  |  |  |  |  |
| Cut-out sealed (Y/N) |  |  |  |  |  |  |  |  |  |  |
| Date Energised |  |  |  |  |  |  |  |  |  |  |

| I hereby confirm that Electricity Services have been installed to the above referenced Street Furniture as described above |  |
| --- | --- |
| Signed: | For and on behalf of (Company name): |
| Print name: | Job title: |
|  | Date: |