## Front Sheet
Earth Measurement Template for Fall of Potential Results
This template should be used to record Fall of Potential earth mat measurements. Earth measurements should be taken in accordance with:- • Section 13 of CoP333 “Earthing Design for 11/6.6kV Distribution Substations and Equipment”, and • Electricity Specification 220 “Pre-commissioning Requirements for Independent Connection Providers Requiring New Assets to be Connected to the 11/6.6kV Network” • ENA TS 41-24 - Guidelines for the Design, Installation, Testing and Maintenance of Main Earthing Systems in Substations Earthing measurements are one of the requirements to be met before a proposed new substation can be energised and failure to provide the requested earthing information to an adequate standard could delay energisation.
Last Updated |  | 22.01.2019

## Results Template
Please refer to the Front Sheet for relevant standards
Please complete these green cells
FALL OF POTENTIAL MEASUREMENTS AT:
SUBSTATION NAME:
SUBSTATION NUMBER:
POST CODE:
ENWL REFERENCE NUMBER:
TEST REF | P2 Distance from C1 (WITH C2 @ 50M) | 2 m | 10 m | 20 m | 25 m | 29 m | 30 m | 31 m | 32 m | 33 m | 35 m | 40 m | 45 m
| C1 Earth under test Ω | Earth test measurements (Ohms - Ω)
1 | LV MAT
2 | HV MAT
3 | HV RADIAL
4 | HV MAT + HV RADIAL
5 | LV MAT + HV MAT + HV RADIAL
Procedure for 4 terminal earth tester :
WARNING: only applicable to substations not connected to HV network
A) Choose a suitable route avoiding metallic pipes and cables which
can interfere with the accuracy of the tests (insulated sheathed cables are ok).
B) Disconnect all earths from the earth bar.
C) Run out C2 (red lead) to ground spike at 50 metres from the substation.
D) Connect C1 and P1 leads to the LV mat earth with P2 at 2 metres
E) Carry out test No 1 at 2M
F) Connect C1 and P1 leads to the HV mat earth with P2 at 2 metres.
G) Carry out test No 2 at 2M
H) Repeat the above for tests 3,4 & 5.
I) Repeat the above with P2 between 10 and 45 metres maintaining
a straight line between the points.
Notes; the measurements should vary similar to the graph shown and the true ohmic value occurs at the flattening out position, although this will only be apparent over a few metres. This normally occurs at 62% of the P2 position which would be at 31m with a 50 m lead. However, this may vary if the ground over the 50m is not uniform. On metalled surfaces P2 ground spike may be replaced by a weighted metallic plate. Adequate contact with the surface can be achieved with a cloth soaked in saline placed between the plate and the hard surface. This method works on tarmac, paving slabs and concrete but is inaccurate on reinforced concrete.
NOTES
Completed by:
Company:
Signed:
Date: