appendix a

SCHEDULES OF INFORMATION

Schedule A - Manufacturers and location of manufacturing, inspection and testing

Schedule B - General particulars and guarantees

Schedule C - Ratings

Schedule D - Current and voltage transformers

Schedule E - SF6 gas and enclosure details

Schedule F - Insulators

Schedule G - SF6 gas servicing equipment

Schedule H - List of sub-contractors

Schedule I - List of variations from the specification

Schedule J - Recommended Tools and Spare Parts

Schedule A - Manufacturers and location of manufacturing, inspection and testing (to be completed by the tenderer)

| Item | Manufacturer | Location of Manufacture | Location of testing and inspection |
| --- | --- | --- | --- |
| Main equipment Fabrication of structural steelwork Galvanising Fabrication of aluminium casings Rigid busbars and connections Flexible busbars and connections Insulators Insulator fittings Large porcelains Disconnectors, by-pass and earthing switches Switch disconnectors Circuit breakers Circuit breaker insulators Insulating chambers Protective equipment Protective relays Current transformers Voltage transformers Control and relay panels Instruments Multicore cables Neutral earthing resistances Auxiliary Equipment Motors for circuit breaker equipment Rectifier equipment Contactors |  |  |  |

Schedule A - Manufacturers and location of manufacturing inspection and testing (continued)

| Item | Manufacturer | Location of Manufacture | Location of testing and inspection |
| --- | --- | --- | --- |
| Hydraulic/pneumatic plant & equipment Compressors Compressor motors Air receivers Pipes Pipe joints Stop valves Safety valves Reducing valves Contact making gauges Filters Dryers Pressure maintaining valves Gas handling equipment Compressors Compressor motors Vacuum pumps Vacuum pump motors Gas receivers Pipes Pipe joints Stop valves Reducing valves Contact making gauges Filters Dryers Pressure maintaining valves Temperature compensated pressure switches Overpressure relief devices |  |  |  |

Schedule B - General particulars and guarantees

Schedule B1 - General particulars (these items are declared by the Purchaser)

| Item | Requirement |
| --- | --- |
| Inclusion or exclusion of power and/or control cables from the contract price |  |
| Power supply for electrical operation of circuit breakers, disconnectors and earth switches (a) Closing (b) Opening | 110VDC 110VDC |
| Power supply for compressor operation | 110VDC |
| Supply voltage for auxiliary equipment | 110VDC |
| Finish of control and relay panels | To ENA TS 50-18 “Design and application of ancillary electrical equipment” |
| Provision of voltage transformer HV links |  |
| Provision of three phase auto reclosing (a) High speed (b) Low speed |  |
| Suitability of circuit breakers for later adoption of three phase auto reclosing (a) High speed (b) Low speed |  |

Schedule B2 - Minimum Factors of Safety required for structural and other materials and items used in the construction of the switchgear (these items are declared by the Purchaser)

| Item | F of S |
| --- | --- |
| Busbars or other connections, based upon an elastic limit or other 0.1% proof stress | 2.5 |
| Fully assembled insulator units, based upon mechanical test | 2.5 |
| Insulator fittings based upon mechanical test | 2.5 |
| Steel structures based upon elastic limit of tension members and on crippling loads of compression members | 2.5 |
| Structure foundations against overturning or up-rooting under maximum simultaneous imposed working load. | 2.5 |

Schedule B3 - Quality of materials (to be completed by Tenderer)

Ferrous materials

| Particulars | Steel structures, circuit breakers, operating rods, etc. |  |  |  | Insulator fittings |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Cast Steel | Sections & plates | Fasteners |  | Steel | Malleable cast Iron |
|  |  | Steel | Steel |  |  |  |
|  |  |  | High tensile | Mild Steel |  |  |
| 1. Tensile breaking strength MN/m² 2. Elongation on breaking percentage 3. Gauge length of specimen 4. Diameter of specimen mm 5. Elastic limit as percentage of breaking strength 6. Modulus of elasticity MN/m² |  |  |  |  |  |  |

Non - Ferrous materials

| Material | Specification or analysis |
| --- | --- |
| 1. Casings for current carrying components 2. Conductors 3. Other purposes |  |

Schedule C - Ratings

Schedule C1 - Circuit Breakers - to be completed by Tenderer for each type

| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. | Type Type reference of circuit breaker Rated values and characteristics Number of poles Class: Indoor (I) or outdoor (O) Rated voltage (a) Rated lightning impulse withstand voltage to earth and between poles (b) Rated lightning impulse withstand voltage between terminals of open poles (c) Rated 1 minute power frequency withstand voltage Rated frequency Rated normal current Rated line charging breaking current Rated cable charging breaking current Rated (single) capacitor breaking current Rated low inductive breaking current (a) Transformer, frequency 500Hz (b) Reactor, frequency 2 - 3kHz Rated short circuit breaking current (a) Symmetrical single phase (b) Symmetrical three phase (c) Asymmetrical single phase (b) Asymmetrical three phase | kV kV kV Hz A A A A A A A A A A |  |
| --- | --- | --- | --- |

Schedule C1 - Circuit Breakers - to be completed by Tenderer for each type (continued)

| 12. 13. 14. 15. 16. 17. 18. 19. 20. 21. 22. | Rated transient recovery voltage (a) First reference voltage U1 (b) Time to reach U1 - t1 (c) TRV peak value Uc (d) Time to reach Uc - t2 (e) Time delay td (f) Voltage co-ordinate U' (g) Time co-ordinate t' (h) Rate of rise U1/ t1 Rated short circuit making current (a) Peak three phase (b) Peak single phase Rated operating sequence Rated short time current/duration (a) Three phase (b) Single phase Rated out of phase breaking current Opening time without current Minimum break time at rated breaking current Minimum auto reclose dead time following opening under fault conditions Closing time without current Close - open time; maximum time to open following closure onto a prepared trip fault Type tests verifying the above ratings | kV s kV s s kV s kV/s kV kV kA/s kA/s kA ms ms ms ms ms |  |
| --- | --- | --- | --- |

Schedule C1 - Circuit Breakers - to be completed by Tenderer for each type (continued)

| 23. 24. 25. 26. 27. 28. 29. 30. 31. 32. 33. | Constructional features Mass of each installed circuit breaker Shock loading of circuit breaker SF6 gas (a) Total gas quantity in circuit breaker enclosure (b) Normal operating temperature at 20°C (c) Maximum operating temperature at 20°C (d) Low pressure alarm pressure at 20°C (e) Low pressure lock out pressure at 20°C (f) Minimum gas pressure to achieve rated breaking current at 20°C (g) Minimum pressure to withstand two asynchronous rated power frequency voltages across open poles at 20°C (h) Minimum pressure to withstand 1.5 x phase to earth voltage between terminals and earth at 20°C (i) Maximum leakage rate of gas from circuit breaker enclosures (j) Type of filter Number of breaks in series per pole Minimum clearance (a) Between poles (b) To earth Stroke of moving contacts Material of main contacts Material of moving contacts Type of arc control device Type of device used to limit rate of rise of re-striking voltage Resistance across main contacts at rated current | kg kg bar g bar g bar g bar g bar g bar g bar g percentage per annum mm mm mm mm  |  |
| --- | --- | --- | --- |

Schedule C1 - Circuit Breakers - to be completed by Tenderer for each type (continued)

| 34. 35. 36. 37. 38. 39. 40. 41. 42. 43. 44. 45. 46. | Is the contact current used to increase the contact pressure? Material of tank Thickness of tank Routine pressure test on circuit breaker enclosure Type pressure test on circuit breaker enclosure Operating mechanism Type reference of circuit breaker operating mechanism Is the circuit breaker trip free or fixed trip? Method of operating circuit breaker, for example, stored energy Pre-charge pressure of energy storage system Capacity of energy storage system, pump cut in to pump cut out Operating sequences available with stored energy at pump cut out Pneumatic or hydraulic pressures (a) Pump motor cut in (b) Pump motor cut out (c) Close lock out pressure (d) Close lock out reset pressure (e) Trip lock out (f) Trip lockout (g) Low pressure alarm (h) Low pressure alarm reset (i) Safety device operate (j) Safety device reset Pump motor (a) Electrical supply AC or DC? (b) Rated voltage of operation (c) Starting current | bar g bar g bar g litre bar g bar g bar g bar g bar g bar g bar g bar g bar g bar g V A |  |
| --- | --- | --- | --- |

Schedule C1 - Circuit Breakers - to be completed by Tenderer for each type (continued)

| 47. 48. 49. 50. 51. 52. 53. 54. 55. 56. | (d) Operating current (e) Motor speed Type of compressor Type of safety valve Type of non return valve Type of isolating valve Type of pressure switch Closing coils (a) Rated voltage (b) Current to close circuit breaker at rated voltage (c) Minimum operating voltage Trip coils (a) Rated voltage (b) Current to open circuit breaker at rated voltage (c) Minimum operating voltage Current rating and type of auxiliary switches provided State the number of circuit breaker interruptions that may be performed before maintenance is required (a) At the rated current (b) At 10kA (c) At 20kA State the method by which contact wear is externally indicated and/or may be measured | A RPM V A V V A V |  |
| --- | --- | --- | --- |

Schedule C2 - Disconnectors - to be completed by Tenderer for each type

| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. | Type Type reference of disconnector Rated values and characteristics Number of poles Class: Indoor (I) or outdoor (O) Rated voltage Rated insulation level (a) Rated lightning impulse withstand voltage to earth and between poles (b) Rated lightning impulse withstand voltage between terminals of open poles (c) Rated 1 minute power frequency withstand voltage Rated frequency Capacitive current switching ability (a) Making (b) Breaking Rated normal current Rated short time current/duration (a) Three phase (b) Single phase Trip impulse to contact separation time Closing impulse to contact make time Type test to verify the above ratings | kV kV kV kV Hz A A A kA/s kA/s s s |  |
| --- | --- | --- | --- |

Schedule C2 - Disconnectors - to be completed by Tenderer for each type (continued)

| 13. 14. 15. 16. 17. 18. 19. 20. 21. 22. 23. 24. | Constructional features Weight of installed earth switch SF6 gas (a) Minimum pressure to withstand two asynchronous rated power frequency voltages across open poles at 20°C (b) Minimum pressure to withstand 1.5 x phase to earth voltage between terminals and earth at 20°C Minimum clearance (a) Between poles (b) To earth Stroke of moving contacts Material of main contacts Resistance across main contacts at rated current Is the contact current used to increase the contact pressure? Operating mechanism Type reference of operating mechanism Method of operating circuit breaker, for example, stored energy Operating motor (a) Type, AC or DC? (b) Rated voltage (c) Opening current on starting (d) Opening current running (e) Closing current starting (f) Closing current running (g) Speed Method of indicating contact status, OPEN and CLOSED Current rating and type of auxiliary switches provided | kg bar g bar g mm mm mm  V A A A A RPM |  |
| --- | --- | --- | --- |

Schedule C3 - Earth Switches - to be completed by Tenderer for each type

| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. 13. | Type Type reference of earth switch Rated values and characteristics Number of poles Class: Indoor (I) or outdoor (O) Rated insulation level (a) Rated lightning impulse withstand voltage to earth and between poles (b) Rated lightning impulse withstand voltage between terminals of open poles Rated frequency Rated short time current/duration (a) Three phase (b) Single phase Rated short circuit making current (if applicable) Type test to verify the above ratings Constructional features Weight of installed earth switch Minimum clearance between live parts and earth Stroke of moving contacts Material of main contacts Resistance across closed contacts | kV kV kV Hz A A kg mm mm  |  |
| --- | --- | --- | --- |

Schedule C3 - Earth Switches - to be completed by Tenderer for each type (continued)

| 14. 15. 16. 17. 18. | Operating mechanism Type reference of earth switch operating mechanism Method of operating earth switch for example manual or motor Operating motor (a) Type, AC or DC? (b) Rated voltage (c) Opening current on starting (d) Opening current running (e) Closing current starting (f) Closing current running (g) Speed Method of indicating contact position Current rating and type of auxiliary switches provided | V A A A A RPM |  |
| --- | --- | --- | --- |

Schedule D - Current and voltage transformers (to be completed by Tenderer)

Schedule D1 - Current transformers

| 1. | FEEDER UNIT PROTECTION Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |
| --- | --- | --- | --- |
| 2. | FEEDER BACK-UP PROTECTION Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |
| 3. | METERING Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |

Schedule D1 - (to be completed by Tenderer) (continued)

| 4. | INSTRUMENTATION Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |
| --- | --- | --- | --- |
| 5. | BUSBAR PROTECTION DISCRIMINATING Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |
| 6. | BUSBAR PROTECTION CHECK Highest equipment voltage Insulation level Frequency Rated continuous primary thermal current Rated primary/secondary currents Rated output Class of accuracy Rated accuracy limit factor Short time current and duration Rated primary current Nominal turns ratio Knee point emf Vk Maximum secondary winding resistance at 75° C Exciting current at Vk/2 | kV kV Hz A A VA A s A V  V |  |

Schedule D2 - Voltage transformers (to be completed by Tenderer)

| 1. For protection & instrumentation For metering 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. 13. | Type (reference of voltage transformer) Method of transformation (winding configuration) Transformation ratio Rated output per phase Class of accuracy Rated output per phase Class of accuracy Voltage factor Rated time Electrostatic capacity of each capacitor, line to earth Insulating medium Total volume of insulating medium, per single phase unit Weight of complete unit ready for service | VA VA s pF litre kg |  |
| --- | --- | --- | --- |

Schedule E - SF6 gas and enclosure details (to be completed by Tenderer)

| 1. 2. | Number of segregated gas enclosures for each circuit breaker type (a) Single feeder (b) Banked feeder (c) Supergrid transformer (d) Bus section (e) Bus coupler Purpose (insulation, arc extinction or both) and volume of gas in each type of gas enclosure (a) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (b) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (c) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (d) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (e) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (f) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (g) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas (h) Purpose of enclosure Volume of enclosure Weight of enclosed gas Pressure of enclosed gas | m3 kg bar g m3 kg bar g m3 kg bar g m3 kg bar g m3 kg bar g m3 kg bar g m3 kg bar g m3 kg bar g |  |
| --- | --- | --- | --- |

Schedule E - SF6 gas and enclosure details (to be completed by tenderer) (continued)

| 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. 13. 14. 15. 16. 17. 18. | SF6 gas pressures (a) Normal operating pressure at 20°C (b) Pressure falling alarm at 20°C (c) Pressure low alarm at 20°C (d) Pressure high alarm at 20°C (e) Pressure at which safety device operates Type of pressure gauge Type of safety device Type of isolating valve Method of joining piped sections Method of jointing pipes and valves Type of gas filter Material of enclosure casing Thickness of enclosure casing Routine test pressure for enclosures Type test pressure for enclosures Total gas content of installed switchboard Estimated total gas leakage rate of installed switchboard. Withstand voltage of chambers subject to DC voltage when testing power cables Enclosure burn through time at rated earth fault current Shortest time to rupture of a bursting disc at rated short circuit currents | bar g bar g bar g bar g bar g mm bar g bar g kg percentage per Annum kV ms ms |  |
| --- | --- | --- | --- |

SF6 gas details ( at 20C Normal Operating Pressure)

| 1. 2. 3. 4. 5. 6. | Water content - maximum Nitrogen content - maximum Oxygen content - maximum Carbon tetrachloride CCl4 content - maximum Free acidity expressed as HF maximum Hydrolysable fluoride compounds - expressed as F - maximum | mg/kg g/kg g/kg g/kg mg/kg mg/kg |  |
| --- | --- | --- | --- |

Schedule F - Insulators (to be completed by Tenderer)

| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. | Type (Maker's designation) Insulator material Form (conical, disc, etc.) Dimensions Weight of complete insulator Method of bonding to (a) Casing (b) Conductor Material of fittings (a) Casing (b) Conductor Electrostatic capacity of complete insulator Minimum creepage distance over insulator (state if more than one type) String distance over insulator surface between conductor and casing (state type if more than one) Maximum partial discharge magnitude at 67% of rated voltage. Method of drying insulators (a) At works (b) Prior to commissioning (c) After maintenance - state anticipated duration of drying process | mm kg pF mm mm pC |  |
| --- | --- | --- | --- |

Schedule G - SF6 gas servicing equipment (to be completed by Tenderer)

| 1. 2. 3. 4. 5. 6. 7. 8. 9. 10. 11. 12. 13. 14. 15. 16. 17. 18. 19. | Type of plant - static or mobile Type of connection between pumping equipment and (a) New and used gas storage receivers (b) Switchgear Type of compressor Speed of compressor Type of motor Motor rating (BS Rating) Speed of motor at rated output Motor full load current Motor maximum starting current Compressor output (a) At normal working inlet pressure (b) At atmospheric inlet pressure and 20 °C Normal delivery pressure and temperature Type of vacuum pump Speed of vacuum pump Type of motor Motor rating (BS Rating) Speed of motor at rated output Motor full load current Motor maximum starting current Output of vacuum pump (a) At normal working inlet pressure (state pressure at 20 °C) (b) At atmospheric inlet pressure and 20 °C | RPM kW RPM A A litre/min litre/min °C RPM kW RPM A A litre/min litre/min |  |
| --- | --- | --- | --- |

Schedule G - SF6 gas servicing equipment (to be completed by Tenderer)(continued)

| 20. 21. 22. 23. 24. 25. 26. 27. 28. 29. | Type of compressor after cooler (a) Cooling medium (b) Design of cooler (c) Power consumption at maximum gas flow rate Type of gas evaporator unit (a) Heating medium (b) Design of evaporator (c) Power consumption at maximum gas flow rate Number and grouping of storage receivers for (a) New SF6 (b) Used SF6 Water volume of storage receivers for (a) New SF6 (b) Used SF6 Total gas stored at normal operating pressure at 20 °C in storage receivers for (a) New SF6 (Litres at atmospheric pressure and 20 °C) (b) Used SF6 (Litres at atmospheric pressure and 20 °C) Maximum and normal operating pressure in storage receivers for (a) New SF6 (b) Used SF6 Filling ratio of storage receivers Time to extract gas from circuit breaker (all compartments) from normal working pressure to (1) Atmospheric pressure (2) 20 mm mercury pressure Time to evacuate air from circuit breaker (all compartments) to 1 mm mercury pressure Time to evacuate air from largest item of plant (all compartments) from normal working pressure to (1) Atmospheric pressure (2) 20 mm mercury | litre litre bar g bar g hour hour hour hour hour hour |  |
| --- | --- | --- | --- |

Schedule G - SF6 gas servicing equipment (to be completed by Tenderer)(continued)

| 30. 31. 32. 33. 34. 35. 36. 37. 38. 39. 40. 41. 42. 43. 44. 45. | Time to evacuate air from largest item of plant (all compartments) to 1 mm mercury Time recommended for holding vacuum prior to refilling with gas Time to refill equipment with SF6 from vacuum to normal working pressure Rate at which gas in equipment can be re-circulated through filters Maximum pressure that can be applied to connections between servicing equipment and switchgear Maximum pressure that can be applied to compressor inlet Maximum pressure that can be applied to vacuum pump inlet Bursting pressure of bursting discs; state location and pressure Weight of filter material in filters Type of containers for topping up switchgear with SF6 gas Weight of item 39 with full gas load Weight of containers for dry Nitrogen Volume of Nitrogen stored at 15 °C Type of leak detector Type of Oxygen analyser Type of moisture meter | hour hour hour litre/min bar g bar g bar g kg kg kg litre |  |
| --- | --- | --- | --- |

Schedule H - List of sub-contractors

| Name Of Sub-Contractor | Item To Be Supplied |
| --- | --- |

Name of tenderer

Schedule I - List of variations from the specification

| No. of Clause | Details of item not in accordance with the Specification |
| --- | --- |

Name of tenderer

Note: Additional sheets may be inserted as required

Schedule J – Tools and Spare Parts

List of tools recommended for use with each installation

| Description | Price Each £ | Total Price £ |
| --- | --- | --- |

Recommended spare parts, to be ordered at the discretion of the company

| Description | Price Each £ | Total Price £ |
| --- | --- | --- |

Appendix B

SELF-CERTIFICATION CONFORMANCE DECLARATION

CLAUSE BY CLAUSE CONFORMANCE WITH SPECIFICATION

The manufacturer shall declare conformance or otherwise, clause by clause, using the following levels of conformance declaration codes.

Conformance declaration codes

| N/A = | Clause is not applicable/appropriate to the product/service |
| --- | --- |
| C1 = | The product/service conforms fully with the requirements of this clause |
| C2 = | The product/service conforms partially with the requirements of this clause |
| C3 = | The product/service does not conform to the requirements of this clause |
| C4 = | The product/service does not currently conform to the requirements of this clause, but the manufacturer proposes to modify and test the product in order to conform. |

| Manufacturer: |  |
| --- | --- |
| Product/Service Description |  |
| Product /Service Reference : |  |

Assessor

| Name: | Company | Signature | Date |
| --- | --- | --- | --- |

| Clause / Sub-clause |  | Requirement | Conformance Code | Remarks (Must be completed if Conformance Code is not Cs1) |
| --- | --- | --- | --- | --- |
| 1 |  | Scope |  |  |
| 3 | 1 | Product not to be changed |  |  |
| 3 | 2 | Electricity North West technical approval |  |  |
| 3 | 3 | Quality assurance |  |  |
| 3 | 4 | Formulation |  |  |
| 3 | 5 | Identification markings |  |  |
| 3 | 6 | Manufacturers already approved |  |  |
| 3 | 7 | Product conformity |  |  |
| 4 | 1 | Requirement for type tests at the suppliers’premises |  |  |
| 4 | 2 | Requirement for routine tests at the suppliers’ premises |  |  |
| 3 | 3 | Requirement for on-site tests |  |  |
| 5 |  | Technical and Performance Requirements |  |  |
| 5 | 1 | General design features |  |  |
| 5 | 1.1 | Modular construction |  |  |
| 5 | 1.2 | Thermal expansion |  |  |
| 5 | 1.3 | Gas zones |  |  |
| 5 | 1.4 | Robust construction |  |  |
| 5 | 1.5 | Access for Operation, Maintenance and Inspection |  |  |
| 5 | 1.6 | Simplicity of Operation |  |  |
| 5 | 1.7 | Earthing |  |  |
| 5 | 2 | Circuit Breakers |  |  |
| 5 | 2.1 | Type |  |  |
| 5 | 2.2 | Testing and Inspection in an operational configuration |  |  |
| 5 | 2.3 | Small current interrupting duties |  |  |
| 5 | 2.4 | Circuit Breaker Re-striking |  |  |
| 5 | 2.5 | Short Line Faults and out-of-phase switching |  |  |
| 5 | 2.6 | Minimum interruption times |  |  |
| 5 | 2.7 | Transient recovery voltage |  |  |
| 5 | 2.8 | Lock out Facilities |  |  |
| 5 | 2.9 | Ancillary Re-striking Voltage Devices |  |  |
| 5 | 2.10 | Parallel operation |  |  |
| 5 | 2.11 | Auto reclosing |  |  |
| 5 | 2.12 | Continues Operation without Gas Re-charge |  |  |
| 5 | 3 | Circuit breaker operating mechanisms – general requirements |  |  |
| 5 | 3.1 | Type of mechanism |  |  |
| 5 | 3.2 | Capability |  |  |
| 5 | 3.3 | Anti-pumping |  |  |
| 5 | 3.4 | Pole discrepancy |  |  |
| 5 | 3.5 | Operation and Adjustment of Single Phase Units |  |  |
| 5 | 3.6 | Energy Charge and Recharge of Operating Mechanism |  |  |
| 5 | 3.7 | Immunity from Inadvertent Operation |  |  |
| 5 | 3.8 | Operation counter |  |  |
| 5 | 3.9 | Indication of OPEN and CLOSED status |  |  |
| 5 | 3.10 | Manual operation of circuit breakers |  |  |
| 5 | 3.11 | Slow operation for maintenance |  |  |
| 5 | 3.12 | Labelling |  |  |
| 5 | 4 | Circuit breaker operating mechanisms – requirements for hydraulic units |  |  |
| 5 | 4.1 | Pressure indication and monitoring |  |  |
| 5 | 4.2 | Loss of operating pressure in single phase unit |  |  |
| 5 | 4.3 | Excessive time operation of pressure pump |  |  |
| 5 | 4.4 | Accumulator gas pressure |  |  |
| 5 | 4.5 | Accumulator Energy |  |  |
| 5 | 4.6 | Bleeding of hydraulic system |  |  |
| 5 | 4.7 | Hydraulic fluid reserve |  |  |
| 5 | 5 | Circuit breaker operating mechanisms – requirements for spring powered units |  |  |
| 5 | 5.1 | Speed of recharging |  |  |
| 5 | 5.2 | Prevention and indication of slow or incomplete closure |  |  |
| 5 | 5.3 | Manual Charging |  |  |
| 5 | 6 | Disconnector and switch-disconnectors |  |  |
| 5 | 6.1 | Safe maintenance |  |  |
| 5 | 6.2 | Power Operation |  |  |
| 5 | 6.3 | Interlocking – Metallic Screens |  |  |
| 5 | 6.4 | Insulation Level |  |  |
| 5 | 6.5 | Load Currents |  |  |
| 5 | 7 | Maintenance Earthing Switches |  |  |
| 5 | 7.1 | Provision and location of maintenance earthing switches |  |  |
| 5 | 7.2 | Power Operation |  |  |
| 5 | 7.3 | Visual confirmation of operation |  |  |
| 5 | 7.4 | Testing facilities |  |  |
| 5 | 8 | High Speed Earthing Switches |  |  |
| 5 | 8.1 | Method of operation |  |  |
| 5 | 8.2 | Rating |  |  |
| 5 | 8.3 | Location |  |  |
| 5 | 8.4 | Testing facilities |  |  |
| 5 | 8.5 | Interruption of induced currents |  |  |
| 5 | 9 | Combined Disconnector and Earth Switches |  |  |
| 5 | 9.1 | Power Operation |  |  |
| 5 | 9.2 | Visual confirmation of operation |  |  |
| 5 | 10 | Operating Cubicles |  |  |
| 5 | 10.1 | Cubicle Equipment |  |  |
| 5 | 10.2 | Local/remote operation |  |  |
| 5 | 10.3 | Wiring Marshalling |  |  |
| 5 | 10.4 | Demonstration of immunity to electromagnetic interference |  |  |
| 5 | 11 | Interlocking Facilities |  |  |
| 5 | 11.1 | Mechanical interlocking |  |  |
| 5 | 11.2 | Electrical interlocking |  |  |
| 5 | 11.3 | Electrical interlocking of manual operation |  |  |
| 5 | 11.4 | Circuit breaker gas pressure |  |  |
| 5 | 11.5 | Circuit breaker opening |  |  |
| 5 | 11.6 | Interlocking of disconnectors and switch disconnectors |  |  |
| 5 | 11.7 | Interlocking of maintenance and high speed earthing switches |  |  |
| 5 | 11.8 | Free operation under maintenance |  |  |
| 5 | 11.9 | Emergency Operation |  |  |
| 5 | 11.10 | Repeat relays |  |  |
| 5 | 12 | Locking facilities |  |  |
| 5 | 12.1 | Direct local locking |  |  |
| 5 | 12.2 | Locking of Equipment |  |  |
| 5 | 12.3 | Padlocking and Key Cabinet |  |  |
| 5 | 13 | Auxiliary Switched and Contactors |  |  |
| 5 | 13.1 | Sufficiency of provision |  |  |
| 5 | 13.2 | Exclusion of repeat relays |  |  |
| 5 | 14 | Current and Voltage Transformers |  |  |
| 5 | 14.1 | Location of CTs |  |  |
| 5 | 14.2 | Marking and positioning of CTs |  |  |
| 5 | 14.3 | Requirements for CTs |  |  |
| 5 | 14.4 | Dual Ratio CTs |  |  |
| 5 | 14.5 | CT Ratings |  |  |
| 5 | 14.6 | Magnetisation, core loss and secondary resistance curves |  |  |
| 5 | 14.7 | Requirements for VTs |  |  |
| 5 | 15 | Surge Arresters |  |  |
| 5 | 15.1 | Gas insulation of surge arresters |  |  |
| 5 | 15.2 | Protection against excess pressure |  |  |
| 5 | 15.3 | Monitoring of gas pressure |  |  |
| 5 | 15.4 | Insulation level |  |  |
| 5 | 15.5 | Enclosure requirements |  |  |
| 5 | 16 | Power Cable Termination |  |  |
| 5 | 16.1 | Cable boxes |  |  |
| 5 | 16.2 | Cable cleats and cable ancillaries |  |  |
| 5 | 16.3 | Protection from arc products |  |  |
| 5 | 16.4 | Thermal expansion |  |  |
| 5 | 16.5 | Testing voltage and test bushing |  |  |
| 5 | 16.6 | Terminations in unused switch bays |  |  |
| 5 | 16.7 | Testing of switchgear prior to connection of cables |  |  |
| 5 | 17 | Bushings |  |  |
| 5 | 18 | Multicore and auxiliary cables |  |  |
| 5 | 18.1 | Compliance with specification |  |  |
| 5 | 18.2 | Multicore wiring included in this contract |  |  |
| 5 | 18.3 | Multicore cable schedule |  |  |
| 5 | 18.4 | Cable containment |  |  |
| 5 | 18.5 | Cable type |  |  |
| 5 | 19 | Fire Precautions |  |  |
| 5 | 19.1 | General fire precautions |  |  |
| 5 | 19.2 | Minimising the risk of fire and consequential damage |  |  |
| 5 | 20 | Control and indication and alarms |  |  |
| 5 | 20.1 | Local control |  |  |
| 5 | 20.2 | Mimic diagram/standby control panel |  |  |
| 5 | 20.3 | ON/OFF and other indications |  |  |
| 5 | 20.4 | SF6 Alarms |  |  |
| 5 | 20.5 | Alarms |  |  |
| 5 | 21 | Ratings |  |  |
| 5 | 21.1 | Ratings |  |  |
| 5 | 21.2 | Variation of power frequency withstand voltage with gas density |  |  |
| 5 | 22 | Environment, operating conditions and duty |  |  |
| 5 | 22.1 | Service conditions |  |  |
| 5 | 22.2 | Noise |  |  |
| 5 | 22.3 | Emergency operating performance (EOP) |  |  |
| 5 | 23 | Auxiliary Supplies |  |  |
| 5 | 24 | Finish Colour |  |  |
| 5 | 25 | Switchgear, Operating Cubicles and Panels |  |  |
| 5 | 25.1 | Ferruling |  |  |
| 5 | 25.2 | Terminals and Terminal Blocks |  |  |
| 5 | 25.3 | Internal Wiring |  |  |
| 5 | 26 | Special Tools |  |  |
| 6 |  | Erection and Site Assembly |  |  |
| 6 | 1 | Final Erection in Works |  |  |
| 6 | 2 | First Filling of Gas |  |  |
| 6 | 3 | Site Tests |  |  |
| 6 | 4 | Test Equipment |  |  |
| 7 |  | Drawings |  |  |
| 8 |  | Operational Life, Inspection, Maintenance and Training |  |  |
| 8 | 1 | Operational Life |  |  |
| 8 | 2 | Operating and Maintenance manuals |  |  |
| 8 | 3 | Failure Mode, Effect and Cause Analysis |  |  |
| 8 | 4 | Sample Materials |  |  |
| 8 | 5 | Training |  |  |
| 9 |  | Handling of SF6 and Decontamination Procedures |  |  |
| 9 | 1 | Gas Handling Equipment |  |  |
| 9 | 1.1 | Rate of gas transfer |  |  |
| 9 | 1.2 | Vacuum performance |  |  |
| 9 | 1.3 | Operation of gas plant |  |  |
| 9 | 1.4 | Gas analysis |  |  |
| 9 | 1.5 | Decontamination at the end of service lifetime |  |  |
| 10 |  | Variations |  |  |

Additional Notes: