appendix a

SCHEDULES OF INFORMATION

Schedule A 	– General Particulars of Definite Work

Schedule B 	– Commencement Date and Dates of Readiness for Inspection

Schedule C	– Manufacturers and Places of Manufacture, Testing and Inspection

Schedule D1 	– Technical Details

Schedule D2 	– Cable Details

Schedule D3 	– Emergency Rated System Transformers

Schedule D4 	– Design Reference

Schedule D5 	– Additional Items

Schedule E 	– Drawings

Schedule F1 	– Prices and Quantities for Definite Work

Schedule F2 	– Evaluation of Transformer Losses

Schedule G 	– Optional Extras

Schedule H 	– Access Facilities to the Site

Schedule I 	– Proposed Departures from the Requirements of this Specification

Schedule J 	– Prices for Work at the Option of the Purchaser

SCHEDULE A

GENERAL PARTICULARS OF DEFINITE WORK

(Relevant details to be completed by Purchaser)

| Item | Description | Units |  |
| --- | --- | --- | --- |
| 1 | Section(s) for purposes of payments and taking over | - |  |
| 2 | Sub Station Name and Address | - |  |
| 3 | Number of Units required | - |  |
| 4 | Continuous maximum rating (ONAN) | MVA |  |
| 5 | Rated higher voltage between phases | kV |  |
| 6 | Rated lower voltage between phases | kV |  |
| 7 | Unit auxiliary earthing transformer | - |  |
| 8 | Continuous maximum rating | kVA |  |
| 9 | Rated higher voltage between phases | kV |  |
| 10 | Rated lower voltage between phases (no load) | kV | 0.415/0.240 three-phase four wire |

SCHEDULE B

COMMENCEMENT DATE AND DATES OF READINESS FOR INSPECTION

(To be completed by Tenderer)

Commencement Date                                          20

|  | Section(s) for purposes of payments and taking over | - |  |
| --- | --- | --- | --- |
|  | Sub Station Name and Address | - |  |
| Times from Commencement Date:- |  |  |  |
| 1 | Within which detailed drawings shall be submitted for approval | Calendar Months |  |
| 2 | Within which the material shall be ready for inspection and testing | Calendar Months |  |
| 3 | Within which the Contractor will require access to the site | Calendar Months |  |
| 4 | Within which the material shall be delivered to site | Calendar Months |  |
| 5 | Within which the works shall be completed, tested and ready for continuous use | Calendar Months |  |

Required delivery date                                          20

SCHEDULE C

MANUFACTURERS AND PLACES OF MANUFACTURE, TESTING AND INSPECTION

(Relevant details to be completed by Tenderer)

| Item | Manufacturer's Drawing Number and/or Type Designation | Manufacturer | Place of Manufacture | Place of Testing and/or Inspection |
| --- | --- | --- | --- | --- |
| Transformer Complete |  |  |  |  |
| Transformer Core |  |  |  |  |
| Transformer Windings |  |  |  |  |
| Transformer Main Tank |  |  |  |  |
| On-load Tap-change Equipment |  |  |  |  |
| HV Bushings |  |  |  |  |
| LV Bushings |  |  |  |  |
| Neutral Bushings |  |  |  |  |
| Radiators |  |  |  |  |
| Pipework Expansion Devices |  |  |  |  |
| Oil Valves |  |  |  |  |
| Oil Pumps |  |  |  |  |
| Oil Pump Motors |  |  |  |  |
| Fans |  |  |  |  |
| Fan Motors |  |  |  |  |
| Regenerative Breather |  |  |  |  |
| Cables Boxes |  |  |  |  |

SCHEDULE C

MANUFACTURERS AND PLACES OF MANUFACTURE, TESTING AND INSPECTION

(Relevant details to be completed by Tenderer)

| Item | Manufacturer's Drawing Number and/or Type Designation | Manufacturer | Place of Manufacture | Place of Testing and/or Inspection |
| --- | --- | --- | --- | --- |
| Gas and Oil Actuated Relay(s) |  |  |  |  |
| Outdoor Marshalling or Composite Cubicle |  |  |  |  |
| Indoor Control Cubicle |  |  |  |  |
| Temperature Indicating Devices |  |  |  |  |
| Auxiliary Transformer |  |  |  |  |
| Material for Anti-vibration Mounting |  |  |  |  |
| Noise Enclosure |  |  |  |  |
| Pressure relief device |  |  |  |  |
| Transformer Management System |  |  |  |  |
| HV cable connection (if dry or dead break) |  |  |  |  |
| LV cable connection (if dry or dead break) |  |  |  |  |
| Any deviation from this Schedule shall be notified in writing as soon as possible for the Purchasers approval |  |  |  |  |

SCHEDULE D1

TECHNICAL DETAILS

LONG TERM EMERGENCY cyclic RATED SYSTEM TRANSFORMERS

One set to be competed for each MVA rating, vector group and voltage ratio offered.

(To be completed by Purchaser)

| Item | Description | Units |  |
| --- | --- | --- | --- |
| 1 | Section(s) of contract | - |  |
| 2 | Number of transformers required | - |  |
| 3 | Purchaser's serial number(s) | - |  |
| 4a | Continuous ONAN rating | MVA |  |
| b | Emergency long term rated power - 110°C rise | MVA |  |
| 5 | HV winding connections | - | Star/Delta |
| 6 | Loss capitalisation values: |  |  |
|  | - No load loss | £/kW | £2049.20 |
|  | - ONAN normal tap load loss | £/kW | £584.02 |
| 7 | Impedance envelope at 75°C and emergency rated power | - | See Appendix B, Figure 1 |
| 8 | HV terminations | - | See clause 14.2 |
| 9 | Whether protective current transformers to be supplied within the termination | - | Yes/No |
| 10 | 60pF capacitor bushings fitted as standard for Neutral Voltage Displacement protection | - | See clause 14.2 |
| 11 | HV neutral termination | - | See clause 14.3 |
| 12 | LV termination |  | See clause 14.4 |
| 13 | LV neutral termination | - | See clause 14.5 |
| 14 | Cabling details: |  |  |
|  | - Whether armour clamps for cable glands required |  |  |
|  | - HV |  | Yes/No |
|  | - LV |  | Yes/No |
|  | - Whether LV cable ferrules required | - | Yes/No |
|  | - Test voltage of gland insulation | kV | 10kV DC |
| 15 | Whether flange for unit auxiliary transformer required | - | Yes/No |
| 16 | Whether resettable max./min tpi required | - | Yes |
| 17 | Maximum height of installation | mm | 4270 |

SCHEDULE D1 (Continued)

TECHNICAL DETAILS

LONG TERM EMERGENCY cyclic RATED SYSTEM TRANSFORMERS

One set to be competed for each MVA rating, vector group and voltage ratio offered.

(To be completed by Purchaser)

| 18 | Whether anti-vibration mounting required | - | Yes |
| --- | --- | --- | --- |
| 19 | Whether second WTI required (See Schedule G) | - | No |
| 20 | Whether second voltage compounding CT required | - | No |
| 21 | Whether oil sampling valves required | - | Yes |
| 22 | Whether radiators to be galvanised before painting | - | Yes |
| 23 | Type of control cubicle: | - |  |
| 24 | - Outdoor marshalling cubicle | - | Yes |
| 25 | - Indoor control cubicle | - | No |
| 26 | - Outdoor composite cubicle | - | No |
| 27 | - Wall mounted control cubicle | - | No |
| 28 | Tap position indicator scale | - | Type 'A' see Appendix B Figure 2 |
| 29 | Whether load shedding facilities to be wired-up to indoor control cubicle | - | Yes |
| 30 | Number of copies of operating and maintenance instruction required | - | One draft pdf for 1st type of transformer and one final pdf per transformer |
| 31 | No load voltage ratio at normal tap | kV | 33/11 or 33/6.6 |
| 32 | Tap range |  |  |
|  | - +% | % | 5.73 |
|  | - -% | % | 17.16 |
| 33 | Tap step % | % | 1.43 |

SCHEDULE D2

Cable Details

(To be completed by Purchaser)

| SITE |  |
| --- | --- |
| Electricity North West ORDER No |  |
| SUPPLIERS REFERENCE |  |

| CABLE PARTICULARS | HV Line | HV Neutral | LV Line |  | LV Neutral |
| --- | --- | --- | --- | --- | --- |
| Number of Cables |  |  |  |  |  |
| Number of Cores per cable |  |  |  |  |  |
| Type of Cable |  |  |  |  |  |
| Conductor size mm |  |  |  |  |  |
| Overall diameter of cable mm |  |  |  |  |  |
| CABLE BOX TYPE |  |  |  |  |  |
| Dry with Bimold bushings or approved equivalent (Manufacturer to provide cable elbows for all cable connections) |  |  |  |  |  |
| PLINTH DETAILS |  |  |  |  |  |
| Distance in mm between centre lines of main tank and radiator bank |  |  |  | 4500 |  |
| HANDING |  |  |  |  |  |
| Disposition of radiator bank with respect to main tank when viewed from cable box side of the tank |  |  |  | Left Hand side * Right Hand Side * |  |

* Delete as necessary

SCHEDULE D3

LONG TERM EMERGENCY cyclic RATED SYSTEM TRANSFORMERS

(To be completed by Tenderer)

One set to be completed for each MVA rating and voltage ratio offered.

| Item | Description | Units |  |
| --- | --- | --- | --- |
|  | MAGNETIC CIRCUIT |  |  |
| 1. | Core construction: |  |  |
|  | - Taped/banded/bolted limbs | - |  |
|  | - Taped/banded/bolted yokes | - |  |
|  | - Taping/banding material (as applicable) | - |  |
| 2. | Insulation of: |  |  |
|  | - Core bolts | - |  |
|  | - Core bolt washers | - |  |
|  | - Side plates | - |  |
|  | - Core Laminations | - |  |
|  | WINDINGS |  |  |
| 3. | Types and arrangements of: | - |  |
|  | - HV windings | - |  |
|  | - LV windings | - |  |
|  | - Tapping windings (as applicable) | - |  |
|  | - Winding arrangement i.e. core ../..../..../..../.. | - |  |
| 4. | Conductor Insulation: | - |  |
|  | - HV windings |  |  |
|  | - LV windings | - |  |
|  | - Tapping windings (as applicable) | - |  |
| 5. | Oil circulation (e.g. natural/partially directed/directed) to windings: |  |  |
|  | - HV windings |  |  |
|  | - LV windings |  |  |
|  | - Tapping windings (as applicable) |  |  |
| 6. | Short circuit capability: |  |  |
|  | (a) Potential axial thrust for worst fault condition of each winding |  |  |
|  | - HV windings | tonnes |  |
|  | - LV windings | tonnes |  |
|  | - Tapping windings (as applicable) | tonnes |  |
|  | (b) Coil Clamping short circuit withstand capacity |  |  |
|  | - HV windings | tonnes |  |
|  | - LV windings | tonnes |  |
|  | - Tapping windings (as applicable) | tonnes |  |
|  | (c) Current density in windings (at normal tapping positions) |  |  |
|  | - HV windings (LTEC) | A/mm² |  |
|  | - LV windings (LTEC) | A/mm² |  |
|  | - Tapping windings (as applicable) (LTEC) | A/mm² |  |

SCHEDULE D3 (Continued)

LONG TERM EMERGENCY cyclic RATED SYSTEM TRANSFORMERS

(To be completed by Tenderer)

One set to be completed for each MVA rating and voltage ratio offered

| Item | Description | Units |  |
| --- | --- | --- | --- |
|  | PERFORMANCE CHARACTERISTICS |  |  |
| 7. | No load loss at normal tap (excluding cooling plant loss) | kW |  |
| 8. | Cooling plant loss | kW |  |
| 9. | Load losses: |  |  |
|  | - ONAN rating at 65°C maximum winding temperature rise, nominal tapping | kW |  |
|  | - LTEC at 90°C maximum oil temperature at extreme negative tapping (110°C maximum absolute hot spot temperature). LTEC rating reference ambient temperature is 5°C. | kW |  |
| 10 | Sound Pressure Level: |  |  |
|  | - ONAN Rating | dB(A) |  |
|  | - LTEC Rating | dB(A) |  |
|  | TANK AND COOLER |  |  |
| 11. | Thickness of tank: |  |  |
|  | - Sides | mm |  |
|  | - Base | mm |  |
|  | - Cover | mm |  |
| 12. | Thickness of radiator plates | mm |  |
| 13. | Total oil required (including cooling system) | litres |  |
| 14. | Volume of oil to be removed: |  |  |
|  | - To gain access to core earthing link | litres |  |
|  | - To effect in-site change HV bushing | litres |  |
| 15. | Total volume of conservator(s) | litres |  |
| 16. | Volume of oil in conservator between highest and lowest visible levels | litres |  |
| 17. | Continuous rating of oil pump motor | shaft kW |  |
| 18. | Starting current of oil pump motor | Amps |  |
| 19. | Total number of fans | - |  |
| 20. | Nominal diameter of fans | mm |  |
| 21. | Speed of fans | rev/min |  |
| 22. | Continuous rating of each fan motor | shaft kW |  |
| 23. | Starting current of each fan motor | Amps |  |
|  | GENERAL |  |  |
| 24. | Filling medium for transport | - |  |
| 25. | Total weight as installed in service, including cooler plant, all fittings and oil | tonnes |  |
| 26. | Weight of cooler, complete with oil, conservator etc. | tonnes |  |

Schedule D4

Design Reference

(To be completed by Tenderer)

100	Design Reference

The above design reference is applicable to an identical transformer previously supplied to Electricity North West on which the type tests are applicable to the transformer now offered.

Serial number of transformer on which type tests were performed    .......................................

Date of test                 ......................................

Detail differences are:-

Signed

for     :

If the above statement can be completed items 101 to 111 of the following schedule need not be entered.

SCHEDULE D5

Additional Items

(To be completed by Tenderer)

| 101 | Flux density at normal voltage, tap, and frequency |  |  |
| --- | --- | --- | --- |
|  | - Limbs | Tesla |  |
|  | - Yokes | Tesla |  |
| 102 | Type of core joints |  | Mitre/Butt |
| 103 | Grade of core material |  |  |
| 104 | Conductor material: |  |  |
|  | - HV |  |  |
|  | - LV |  |  |
|  | - Tapping |  |  |
| 105 | No load loss at normal voltage and -17.16% tap | kW |  |
| 106 | Impedance voltage at 75%: |  |  |
|  | - on minimum tap | % per MVA |  |
|  | - on normal tap | % per MVA |  |
|  | - on maximum tap | % per MVA |  |
| 107 | Regulation: |  |  |
|  | - at 75% and ONAN rating | % |  |
|  | - at 90% and LTEC rating (110°C rise) | % |  |
|  | - at 115°C and LTEC rating (135°C rise) | % |  |
| 108 | Thermal time constant of oil |  |  |
|  | - ONAN | minutes |  |
|  | - ODAF | minutes |  |
|  | Thermal time constant of windings | minutes |  |
| 109 | Weight of core and winding assembly | tonnes |  |
| 110 | Weight of copper | tonnes |  |
| 111 | Number of cooler elements |  |  |

SCHEDULE E

DRAWINGS

The following is a list of Drawings which shall be submitted by the Tenderer with his tender.

|  | DESCRIPTION | Tenderer's Drawing No |
| --- | --- | --- |
| (a) | A preliminary outline giving side and end elevation and plan of the tank including tap changer, terminals/cable boxes and cooling equipment. The principal dimensions shall be given and parts to be removed for transport shall be indicated. The maximum dimensions and weights not to be exceeded shall also be shown. |  |
| (b) | A preliminary diagram and rating plate. |  |
| (c) | Circuit and wiring diagrams of connections showing electrical control of on-load tap change and forced cooling equipment. |  |
| (d) | A preliminary internal arrangement drawing fully illustrating the type of transformer offered. |  |

SCHEDULE F1

PRICES AND QUANTITIES FOR DEFINITE WORKS

(Relevant Details to be completed by Tenderer)

The prices (other than the provisional sums) entered below include the whole of the definite work specified in this Specification

| 1 | Section(s) for purposes of payment(s) and taking over | - |  |
| --- | --- | --- | --- |
| 2 | Site of Station | - |  |
| 3 | Number of Units required | - |  |
| 4 | Continuous maximum rating | MVA |  |
| 5 | Rated higher voltage between phases | kV |  |
| 6 | Rated lower voltage between phases | kV |  |
| 7 | Number of Unit Auxiliary Transformers required | - |  |
| 8 | Continuous maximum rating | kVA |  |
| 9 | Rated higher voltage between phases (no load) | kV | 0.415/0.240 Three Phase four wire |
| 11 | - Price of each three phase main transformer (Temperature rise tests and Class A impulse tests to be quoted as an extra in Schedule G) | £ |  |
|  | Loss Evaluation (Each main transformer): | - |  |
|  | - Schedule D No load loss £ 2049.20 x kW | £ |  |
|  | - Schedule D load loss (at ONAN rating) £ 584.02 x kW | £ |  |
| 12 | Total evaluated cost: (a+b+c) | £ |  |
| 13 | Price of each Auxiliary Transformer | £ |  |
|  |  | - |  |
| 14 | Total evaluated cost of Section | £ |  |

Work at Time and Material Rates

SCHEDULE F2

EVALUATION OF TRANSFORMER LOSSES

1.	General Requirements

For the purpose of acceptance or rejection of the tender, the tolerance on guaranteed losses shall be in accordance with BS EN 60076-1.

Electricity North West shall have the right to reject a transformer having tested losses, corrected to Continuous Maximum Rating (CMR) and the reference temperature, exceeding either or both of the guaranteed losses when adjusted by the appropriate tolerance.

2.	Evaluation of Test Losses and Contract Price Variation

The values of no-load and load losses obtained on test, corrected to CMR and the reference temperature where necessary, shall be used to determine a total evaluated cost of loss and shall be compared with the total evaluated guaranteed losses.

Cooler losses shall not be taken into account.  The relevant rates of loss evaluation shall be those declared in Schedule F1.

Based on the comparison stated above, the contract price may be varied in accordance with the provisions stated below but in no case shall be an increase in the contract price if: -

i)	The test impedance on any tapping falls outside the impedance envelope in Appendix B.

ii)	Individually either the no-load or load loss exceeds its guaranteed value plus the BS EN 60076 tolerance.

Variations to the contract price shall be calculated to the nearest pound sterling, values of one half being rounded up.

3.	Calculations of Penalty/Bonus Payment

(a)	For transformers where the total evaluated cost of losses is neither greater than 105% nor less than 95% of the total evaluated guaranteed losses, no variation to the contract price shall be made.

(b)	For transformers where the total evaluated cost of losses exceeds 105% of the evaluated guaranteed losses, the contract price shall be reduced by two times the difference between the total evaluated cost of losses and 105% of the total evaluated guaranteed losses.

(c)	Subject to Clause 2 for transformers with a total evaluated cost of losses less than 95% but not less than 90% of the total evaluated guaranteed losses, the contract price shall be increased by half the difference between the total evaluated cost of losses and 95% of the total evaluated guaranteed losses.

(d)	Subject to Clause 2 for transformers with a total evaluated cost of losses less than 90% of the total evaluated guaranteed losses, the contract price shall be increased by the different between the total evaluated cost of losses and 92½% of the total evaluated guaranteed losses.

SCHEDULE G

Optional Extras

| Item | Price (£) |
| --- | --- |
| Addition of 33kV neutral bushing |  |
| Cable box |  |
| 19kV/63.5V Voltage transformer |  |
| Addition of 50kVA unit auxiliary transformer |  |
| Addition of 100kVA unit auxiliary transformer |  |
| Addition of isolating valves on each cooler element, total for transformer |  |
| Addition of cooling reduction measures |  |
| Addition of second WTI (Capillary type) (38MVA only) |  |
| Addition of capacitor bushings |  |
| Addition of island layer insulation in glands |  |
| Addition of equipment to create a separate cooler bank |  |
| Extra for Type Testing (one set) |  |
| Full set of type tests as specified |  |
| Extra for Special Routine Test (per transformer) |  |
| Discharge tests (to be taken during routine induced over voltage tests) |  |
| Oil leakage test (Clause 26.2.17) |  |
| Extra for Special Paint Finish |  |
| Additional Paint system for adverse service environment. |  |

SCHEDULE H

ACCESS FACILITIES TO THE SITE

(To be completed by Purchaser)

| 1 | Section |  |
| --- | --- | --- |
| 2 | Site of station |  |
| 3 | Ordnance Survey Grid Reference |  |
| 4 | Whether direct road access is available to the site |  |
| 5 | Approximate distance from the site to the nearest road |  |
| 6 | Whether transport by rail is required |  |
| 7 | Whether there is a railway siding near to the site |  |
| 8 | Nearest railway goods station and appropriate distance from the site to the nearest goods station |  |
| 9 | Whether there are any known transport restrictions in the immediate locality of site |  |

Schedule I

PROPOSED DEPARTURES FROM THE REQUIREMENTS OF THis Specification

(To be completed by the Tenderer)

| Section and Clause No | Proposed departures from the requirements of this Specification, with details of alternative proposals |
| --- | --- |

SCHEDULE J

PRICES FOR WORK AT THE OPTION OF THE PURCHASER

| Item | Description | Price of each item £ |
| --- | --- | --- |
| 1. | Extra for supply and fitting of anti-vibration pads | To be included in main price |
| 2 | Extra for noise enclosure if required from the outset | - |
| 3 | Extra for full type tests |  |
| 4 | Extra for discharge tests |  |
| 5 | Extra for oil leakage tests |  |
| 6 | Recommended spares |  |
|  | - HV bushing insulator complete (per bushing) |  |
|  | - HV neutral bushing insulator complete (per bushing) |  |
|  | - LV bushing insulator complete (per bushing) |  |
|  | - LV neutral bushing insulator complete (per bushing) |  |
|  | - HV Cable box bushing insulator complete (per bushing) |  |
|  | - LV Cable box bushing insulator complete (per bushing) |  |
|  | - Any other recommended spares |  |

Appendix c

SELF CERTIFICATION CONFORMANCE DECLARATION

CLAUSE BY CLAUSE CONFORMANCE WITH THIs Specification

The manufacturer shall declare conformance or otherwise, clause by clause, using the following levels of conformance declaration codes.

Conformance declaration codes

| N/A = | Clause is not applicable/appropriate to the product/service. |  |  |
| --- | --- | --- | --- |
| C1 = | The product/service conforms fully with the requirements of this clause. |  |  |
| C2 = | The product/service conforms partially with the requirements of this clause. |  |  |
| C3 = | The product/service does not conform to the requirements of this clause. |  |  |
| C4 = | The product/service does not currently conform to the requirements of this clause, but the manufacturer proposes to modify and test the product in order to conform. |  |  |
| Manufacturer: |  |  |  |
| Product/Service Description |  |  |  |
| Product /Service Reference : |  |  |  |

Assessor

| Name: |  |  | Company s |  | Signature |  | Date |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause/Sub-Clause |  | Requirement |  | Conformance Code |  | Remarks (Must be completed if Conformance Code is not Cs1) |  |  |
| 4 |  | Standards |  |  |  |  |  |  |
| 5 | 1 | Product not to be changed |  |  |  |  |  |  |
| 5 | 2 | Electricity North West Technical Approval |  |  |  |  |  |  |
| 5 | 3 | Quality Assurance |  |  |  |  |  |  |
| 5 | 4 | Formulation |  |  |  |  |  |  |
| 5 | 5 | Identification Markings |  |  |  |  |  |  |
| 5 | 6 | Minimum Life Expectancy |  |  |  |  |  |  |
| 5 | 7 | Product Conformity |  |  |  |  |  |  |
| 6 |  | Requirements for Type and Routine Testing |  |  |  |  |  |  |
| 7 |  | Design |  |  |  |  |  |  |
| 8 |  | Rated Power |  |  |  |  |  |  |
| 9 |  | Tappings |  |  |  |  |  |  |
| 10 |  | Losses |  |  |  |  |  |  |
| 11 | 1 | Noise Requirements |  |  |  |  |  |  |
| 11 | 2 | Sound Power Levels |  |  |  |  |  |  |
| 12 |  | Impedance |  |  |  |  |  |  |
| 13 |  | Terminal Arrangements |  |  |  |  |  |  |
| 14 | 1 | Cable Termination Enclosures |  |  |  |  |  |  |
| 14 | 2 | HV Terminals |  |  |  |  |  |  |
| 14 | 3 | HV Neutral |  |  |  |  |  |  |
| 14 | 4 | LV Terminals |  |  |  |  |  |  |
| 14 | 5 | LV Neutral |  |  |  |  |  |  |
| 14 | 6 | Unit Auxiliary Transformer |  |  |  |  |  |  |
| 15 |  | General Arrangement |  |  |  |  |  |  |
| 16 |  | Tanks and Covers |  |  |  |  |  |  |
| 17 |  | Gaskets |  |  |  |  |  |  |
| 18 |  | Oil |  |  |  |  |  |  |
| 19 | 1 | Cooling Plant |  |  |  |  |  |  |
| 19 | 2 | Gas and Oil Actuated Relay |  |  |  |  |  |  |
| 19 | 3 | Pressure Relief Device |  |  |  |  |  |  |
| 19 | 4 | Winding Temperature Indicator |  |  |  |  |  |  |
| 19 | 5 | Current Transformers |  |  |  |  |  |  |
| 19 | 6 | Other Fittings |  |  |  |  |  |  |
| 19 | 7 | Conservator Level Indicators |  |  |  |  |  |  |
| 19 | 8 | Breathers |  |  |  |  |  |  |
| 19 | 9 | Accessibility |  |  |  |  |  |  |
| 19 | 10 | On-Load Tap Changers |  |  |  |  |  |  |
| 19 | 11 | Pump Flow Meter |  |  |  |  |  |  |
| 20 |  | Valves |  |  |  |  |  |  |
| 21 |  | Cleaning and Painting |  |  |  |  |  |  |
| 22 | 1 | Outdoor Marshalling Cubicle |  |  |  |  |  |  |
| 22 | 2 | Indoor Tap Change Cubicle |  |  |  |  |  |  |
| 23 |  | Automatic Voltage Control Scheme |  |  |  |  |  |  |
| 24 |  | Data Schedules |  |  |  |  |  |  |
| 25 |  | ENA Standard Drawings |  |  |  |  |  |  |
| 26 |  | Telecontrol |  |  |  |  |  |  |
| 27 |  | Transformer Management Systems |  |  |  |  |  |  |
| 28 | 1 | Drawings |  |  |  |  |  |  |
| 28 | 2 | Assembly, Operating and Maintenance Instructions |  |  |  |  |  |  |
| 28 | 3 | Models and Samples |  |  |  |  |  |  |
| 29 | 1 | Tests Before Delivery |  |  |  |  |  |  |
| 29 | 2 | Details of Tests |  |  |  |  |  |  |
| 29 | 3 | Tests After Delivery |  |  |  |  |  |  |
| Schedule B |  | Commencement date and Dates of Readiness for Inspection |  |  |  |  |  |  |
| Schedule C |  | Manufacturers and Places of Manufacture, Testing and Inspection |  |  |  |  |  |  |
| Schedule D3 |  | Long Term Emergency Cyclic Rated System Transformers |  |  |  |  |  |  |
| Schedule D4 |  | Design Reference |  |  |  |  |  |  |
| Schedule D5 |  | Additional Items |  |  |  |  |  |  |
| Schedule E |  | Drawings |  |  |  |  |  |  |
| Schedule F1 |  | Prices and Quantities for Definite Works |  |  |  |  |  |  |
| Schedule F2 |  | Evaluation of Transformer Losses |  |  |  |  |  |  |
| Schedule G |  | Optional Extras |  |  |  |  |  |  |
| Schedule I |  | Proposed Departures from the Requirements of This ES |  |  |  |  |  |  |
| Schedule J |  | Prices for Work at the option of the Purchaser |  |  |  |  |  |  |

Additional Notes: