## 1) User Guide and Network Maps
User Guide
With this tool we aim to provide our customers with information on where there is spare capacity for new developments to connect to our network without triggering reinforcement work. To aid our customers in interpreting the information contained within this tool we have produced a user guide which can be found below. Please note that the data presented in this tool is based on high level analysis and as such may differ from the results of a formal connection application. If your proposed development falls within an area with limited network capacity please contact us to discuss a possible solution. We will always to work with customers to overcome network constraints whether this is through traditional reinforcement or smart network solutions.
Map Data
We now publish an interactive map on our website that contains the same information as contained within this tool.
Click here to access the map.
| Last Updated* | 2026-06-30
This version is 1 day old
* due to the infrequency of EHV plant replacement, switchgear ratings are checked quarterly
| Switchgear ratings checked | 2026-05-15
This version is 46 days old

## 2) 11 kV & 6.6 kV Connections
11 kV & 6.6 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab. Please note that the value of headroom quoted by this tool is based on total capacity available for new connections, the column beside it shows the maximum size of a single connection, based on the on-site primary switchgear rating, which can be much lower. To reflect this the 'Can Connect?' RAG value is derived using the lowest of these two values. It is normally not possible to accommodate a single connection of more than 7 MW at 11 kV or 6.6 kV, this is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations. It is possible that due to these addtional factors and the point of connection requested that the maximum connection size is lower than the values shown below.
Inputs | [18 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest primary substations to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. The results are based on both local constraints and constraints at the associated BSP. | [10 empty] | RAG | Limiting factor: Headroom |  | Limiting factor: Switchgear rating
Northing |  | Enter Data | [17 empty] | Capacity <90% of headroom |  | Suitable
Capacity (MW) |  | Enter Data | [17 empty] | Capacity >90% & < 100% of headroom |  | N/A
Connection Type |  | Enter Data | [17 empty] | Capacity >100% of headroom |  | Unsuitable
Distribution Network Capacity Capacity | [18 empty] | Transmission Constraints (App G)
No | Distance (km) | Primary Substation |  |  | BSP Group |  |  | BCA Group (GSP) |  |  | Primary Substation Location |  | Headroom (MW) | Max Single circuit connection (MW) |  | Can Connect? (RAG) | Can Connect? (RAG) | Limiting factor | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[11 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | - | - | - | #N/A | #N/A | #N/A | #N/A | #N/A | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network through step up transformers.
Generation Synchronous (HV) |  |  |  |  | Generation such as diesel or gas turbines connected to the HV network directly i.e. without step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 3) 33 kV Connections
33 kV Connections
The results given by this tool are based on high level approximations only. It should also be noted that the network may have changed since the last time the data was updated. As such, the outcome of a formal application may differ from the results given by this tool. For further information on how to interpret the data contained within this workbook please refer to the user guide embedded within the first tab.
Please note that the value of headroom quoted by this tool is based on total capacity available for new connections not the maximum size of a single connection which can be much lower. It is normally not possible to accommodate a single connection of more than 40 MW at 33 kV. This is based on the typical load rating of items of plant such as circuit breakers, current transformers and cable terminations.
Inputs | [11 empty] | Key
Easting |  | Enter Data | [5 empty] | Use the controls to the left to find the nearest BSP to your site. The results will be displayed in the table below. When the desired site capacity and connection type are entered an estimate of available headroom and connection feasibility will be displayed. It should be noted that the network assets surrounding your site may not be fed from the closest BSP. |  |  |  |  | Capacity <90% of headroom
Northing |  | Enter Data | [10 empty] | Capacity >90% & < 100% of headroom
Capacity (MW) |  | Enter Data | [10 empty] | Capacity >100% of headroom
Connection Type |  | Enter Data
Distribution Network Capacity Capacity | [11 empty] | Transmission Constraints (App G)
No | Distance (km) | BSP |  |  | BCA Group (GSP) |  |  | BSP Location |  | Headroom (MW) | Can Connect? (RAG) | Materiality Headroom (MW) | Fault Level Headroom (kA) | Transmission System Comment (see tab 6 for more details)
[8 empty] | Easting | Northing
1 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
2 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
3 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
4 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
5 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
6 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
7 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
8 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
9 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
10 | - | - | - | - | - | - | - | - | - | - | 100000 | - | - | -
Connection Types
Demand Firm |  |  |  |  | The connection of load which is secure for a first circuit outage.
Demand N-0 |  |  |  |  | The connection of load which can be actively constrained off under outage conditions.
Generation Synchronous (LV) |  |  |  |  | Generation such as diesel or gas turbines connected to the EHV network through step up transformers.
Generation Inverter Based |  |  |  |  | Generation technologies connected by inverters this typically includes solar and wind generators .
Battery Energy Storage |  |  |  |  | Inverter connected battery energy storage schemes.

## 4) Primary Headroom Data
Primary Substation Headroom
Primary Substation | Voltage (kV) | BSP Group |  | BCA Group (GSP) | Primary Substation Location |  | Individual Circuit Capacity |  | Demand Headroom (MW) |  | Generation Headroom N-0 -(MW) |  |  | Battery Storage Headroom N-0 -(MW)
[5 empty] | Easting | Northing | CB Rating | MVA | Firm | N-0 | Inverter Based | Synchronous - LV | Synchronous - HV
ALBION ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367434 | 426087 | 400 | 4.5726 | 8.6816 | 13.3186 | 22.6154 | 3.9463 | 2.8918 | 13.3186 | 0 | 0 | Connections Reform
ALDERLEY & CHELFORD | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385044 | 379026 | 400 | 7.621 | 7.6878 | 17.4919 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | Connections Reform
ALSTON | 11 | PENRITH & SHAP | PENRITH | HUTTON | 372125 | 546499 | 400 | 7.621 | 0 | 0.895 | 3.1134 | 3.1134 | 3.1134 | 0.895 | 3.2626 | 1.1073 | Connections Reform
AMBLESIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 337602 | 503506 | 400 | 7.621 | 7.179 | 17.0376 | 28.7346 | 18.8828 | 13.837 | 17.0376 | 0 | 0 | Connections Reform
ANCOATS NORTH T11 & T12 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385022 | 398830 | 400 | 4.5726 | 0.098938 | 4.2359 | 32.0759 | 6.488 | 4.7338 | 4.2359 | 4.8939 | 0.33304 | Connections Reform
ANCOATS NORTH T14 | 6.6 | RED BANK | RED BANK | WHITEGATE | 385032 | 398840 | 400 | 4.5726 | 2.3615 | 7.1115 | 20.8769 | 20.8769 | 15.6148 | 7.1115 | 15.7536 | 7.6053 | Connections Reform
ANNIE PIT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300011 | 527810 | 400 | 7.621 | 4.3602 | 10.7474 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
ANSDELL | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 334416 | 428229 | 800 | 9.1452 | 6.9544 | 9.9544 | 20.7499 | 9.3292 | 6.8068 | 9.9544 | 0 | 0 | Connections Reform
ARDWICK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384753 | 397415 | 630 | 7.2019 | 0 | 2.1549 | 11.2179 | 1.9575 | 1.4344 | 2.1549 | 1.4344 | 0 | Connections Reform
ARNSIDE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 346495 | 478180 | 400 | 7.621 | 7.179 | 13.4612 | 18.3256 | 18.3256 | 13.837 | 13.4612 | 0 | 0 | Connections Reform
ASHTON (GOLBORNE) | 6.6 | ORRELL | ORRELL | WASHWAY FARM / KIRKBY | 357056 | 400663 | 800 | 9.1452 | 0 | 0.30159 | 22.6759 | 8.8625 | 6.4663 | 0.30159 | 5.9845 | 2.5354 | #N/A
ASHTON (RIBBLE) | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 350275 | 430526 | 630 | 7.2019 | 1.282 | 1.282 | 5.1702 | 1.9575 | 1.4344 | 1.282 | 1.4344 | 0 | Connections Reform
ASHTON ON MERSEY | 6.6 | SALE | SALE | CARRINGTON | 377188 | 392252 | 630 | 7.2019 | 7.9493 | 11.5432 | 28.9714 | 8.6648 | 6.3221 | 11.5432 | 6.5315 | 13.4847 | Connections Reform
ASHTON UNDER LYNE T11 & T12 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393275 | 399319 | 630 | 7.2019 | 5.4713 | 9.6083 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
ASHTON UNDER LYNE T13 | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 393285 | 399329 | 630 | 7.2019 | 6.9845 | 11.7345 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
ASHWOOD DALE | 6.6 | BUXTON | BUXTON | STALYBRIDGE | 406537 | 373050 | 630 | 7.2019 | 0 | 0 | 31.2952 | 10.2053 | 7.446 | 0 | 1.3561 | 10.6051 | Connections Reform
ASKAM | 11 | ULVERSTON | ULVERSTON | HARKER | 321558 | 477806 | 630 | 12.0031 | 4.6623 | 11.6423 | 8.6709 | 6.4818 | 4.6586 | 8.6709 | 6.4697 | 8.428 | Connections Reform
ASKERTON CASTLE | 11 | - | - | HARKER | 354779 | 568913 | 800 | 15.242 | 0.9707 | 1.6707 | 3.2047 | 3.2047 | 3.2047 | 1.6707 | 3.9789 | 1.6295 | Connections Reform
ASPATRIA | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 314417 | 542840 | 400 | 7.621 | 4.3223 | 6.3223 | 7 | 1.9575 | 1.4344 | 6.3223 | 0 | 0 | Connections Reform
ATHERTON TOWN CENTRE | 11 | ATHERTON | ATHERTON | KEARSLEY | 367546 | 403338 | 800 | 15.242 | 8.305 | 16.8357 | 31.2172 | 5.1397 | 3.694 | 16.8357 | 3.7461 | 0 | Connections Reform
ATHLETIC ST | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385381 | 432208 | 400 | 4.5726 | 4.3547 | 7.8547 | 22.4723 | 12.8473 | 9.3737 | 7.8547 | 9.6723 | 7.1892 | Connections Reform
AVENHAM | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 354028 | 429192 | 800 | 9.1452 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
BAGULEY | 11 | SALE | SALE | CARRINGTON | 380562 | 389035 | 400 | 7.621 | 6.915 | 11.5432 | 29.737 | 10.0166 | 7.1991 | 11.5432 | 7.6584 | 8.6278 | Connections Reform
BAMBER BRIDGE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 356431 | 426698 | 630 | 12.0031 | 6.5739 | 10.7109 | 11.2179 | 1.9575 | 1.4344 | 10.7109 | 1.4344 | 10.2623 | Connections Reform
BARBARA ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370695 | 407609 | 630 | 7.2019 | 0 | 6.7684 | 11.2179 | 1.9575 | 1.4344 | 6.7684 | 1.4344 | 9.8525 | Connections Reform
BARROW | 11 | BARROW & SANDGATE | BARROW | HARKER | 319709 | 470489 | 630 | 12.0031 | 13.6459 | 18.1459 | 20.2251 | 10.2452 | 7.3634 | 18.1459 | 8.0292 | 18.3194 | Connections Reform
BARTON DOCK RD | 6.6 | BARTON | BARTON | CARRINGTON | 378864 | 395534 | 630 | 7.2019 | 0 | 4.9478 | 11.2179 | 1.9575 | 1.4344 | 4.9478 | 1.4344 | 10.2441 | Connections Reform
BEDFORD | 11 | ATHERTON | ATHERTON | KEARSLEY | 366258 | 399876 | 800 | 15.242 | 4.4627 | 8.9627 | 28.7162 | 10.1251 | 7.2771 | 8.9627 | 7.2768 | 0 | Connections Reform
BELGRAVE | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393008 | 403366 | 630 | 7.2019 | 8.0635 | 11.3681 | 23.8473 | 13.657 | 9.9646 | 11.3681 | 9.5768 | 4.6017 | Connections Reform
BENCHILL | 11 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382454 | 388020 | 400 | 7.621 | 7.7206 | 9.7206 | 11.048 | 1.9575 | 1.4344 | 9.7206 | 1.4344 | 9.8921 | Connections Reform
BENTHAM | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 366887 | 470130 | 400 | 7.621 | 1.0417 | 5.5417 | 6.9596 | 6.9596 | 6.9596 | 5.5417 | 0 | 0 | Connections Reform
BISPHAM | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331655 | 439667 | 630 | 7.2019 | 5.5672 | 10.2042 | 11.2179 | 1.9575 | 1.4344 | 10.2042 | 1.4344 | 10.1499 | Connections Reform
BLACKBULL | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353041 | 433005 | 630 | 7.2019 | 1.0169 | 5.1539 | 11.2179 | 1.9575 | 1.4344 | 5.1539 | 1.4344 | 6.4123 | Connections Reform
BLACKBURN | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 370584 | 429294 | 400 | 4.5726 | 5.5845 | 10.2215 | 30.7308 | 9.5959 | 7.0015 | 10.2215 | 6.1854 | 10.7604 | Connections Reform
BLACKFRIARS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383030 | 399104 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
BLACKLEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 383882 | 403258 | 630 | 7.2019 | 10.133 | 14.77 | 29.8365 | 13.1291 | 9.5793 | 14.77 | 9.7958 | 15.68 | Connections Reform
BLACKPOOL | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330835 | 435308 | 630 | 7.2019 | 12.7091 | 20.4591 | 34.9848 | 8.7465 | 6.3817 | 20.4591 | 6.7082 | 17.439 | Connections Reform
BOLLINGTON | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 393042 | 377873 | 630 | 12.0031 | 2.74 | 2.74 | 11.2179 | 1.9575 | 1.4344 | 2.74 | 1.4344 | 0 | offer signed 25/04/2025
BOLTON BY BOWLAND | 11 | PADIHAM | PADIHAM | PADIHAM | 378320 | 449559 | 400 | 7.621 | 0 | 4.2966 | 8.3266 | 8.3266 | 8.3266 | 4.2966 | 8.4802 | 3.8465 | Connections Reform
BOLTON LE SANDS | 11 | LANCASTER | LANCASTER | HEYSHAM | 347707 | 467237 | 400 | 7.621 | 7.0231 | 10.5231 | 11.2179 | 1.9575 | 1.4344 | 10.5231 | 1.5151 | 5.0572 | Connections Reform
BOTANY BAY | 11 | LEYLAND | LEYLAND | PENWORTHAM | 359442 | 418850 | 630 | 12.0031 | 2.2064 | 10.2064 | 19.9085 | 19.9085 | 19.2175 | 10.2064 | 19.2177 | 9.8578 | Connections Reform
BOW LANE | 11 | LEYLAND | LEYLAND | PENWORTHAM | 354895 | 422392 | 400 | 7.621 | 2.6823 | 7.3193 | 28.3593 | 6.4341 | 4.6243 | 7.3193 | 3.7567 | 5.6289 | Connections Reform
BOWATERS | 11 | BARROW & SANDGATE | BARROW | HARKER | 319579 | 472480 | 400 | 7.621 | 13.6251 | 34.1251 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Connections Reform
BOWDON | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376743 | 386810 | 400 | 7.621 | 0 | 2.9697 | 31.0828 | 12.1464 | 8.7299 | 2.9697 | 8.9022 | 10.8219 | Connections Reform
BRADFORD | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387613 | 397710 | 400 | 4.5726 | 0 | 2.1342 | 11.2179 | 1.9575 | 1.4344 | 2.1342 | 1.4344 | 0 | Connections Reform
BRADSHAWGATE | 6.6 | BOLTON | BOLTON | KEARSLEY | 371891 | 408910 | 400 | 4.5726 | 8.8215 | 19.4615 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
BRAMHALL | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 389440 | 386463 | 630 | 12.0031 | 5.6182 | 9.1182 | 23.1379 | 12.5687 | 9.0334 | 9.1182 | 9.1136 | 8.37 | Connections Reform
BRIDGEWATER | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383543 | 397628 | 800 | 9.1452 | 0 | 4.6668 | 30.7835 | 13.2683 | 9.6809 | 4.6668 | 9.8568 | 6.6125 | Connections Reform
BRINKSWAY | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 388434 | 389885 | 400 | 4.5726 | 7.4409 | 12.0779 | 29.9689 | 12.7767 | 9.3222 | 12.0779 | 9.4256 | 12.706 | Connections Reform
BROADHEATH | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 376412 | 389026 | 400 | 7.621 | 10.2285 | 15.1285 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Connections Reform
BROADWAY | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 344792 | 464471 | 630 | 7.2019 | 12.9914 | 17.1284 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.5151 | 5.0572 | Connections Reform
BUCKSHAW | 11 | LEYLAND | LEYLAND | PENWORTHAM | 356748 | 421312 | 630 | 12.0031 | 12.8265 | 17.8719 | 28.5363 | 13.7157 | 9.8577 | 17.8719 | 9.8081 | 10.2615 | Connections Reform
BURNLEY | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385569 | 434469 | 400 | 4.5726 | 11.4127 | 16.5904 | 21.3275 | 4.8449 | 3.535 | 16.5904 | 3.8058 | 9.6649 | Connections Reform
BURNLEY CENTRE | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384308 | 432288 | 630 | 7.2019 | 4.7308 | 8.8678 | 29.1718 | 11.0456 | 8.0592 | 8.8678 | 6.7909 | 5.3989 | Connections Reform
BURNLEY NORTH | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 384418 | 434168 | 630 | 7.2019 | 3.1242 | 11.4212 | 17.663 | 17.663 | 16.8633 | 11.4212 | 17.1739 | 8.8706 | Connections Reform
BURROW BECK | 11 | LANCASTER | LANCASTER | HEYSHAM | 347903 | 458401 | 630 | 12.0031 | 3.5315 | 8.0913 | 9.4369 | 1.5537 | 1.1167 | 8.0913 | 0.7451 | 5.0572 | Connections Reform
BURSCOUGH BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344595 | 412486 | 630 | 12.0031 | 0 | 0 | 15.4871 | 8.8416 | 6.3546 | 0 | 4.4683 | 2.8737 | Connections Reform
BURY TOWN CENTRE | 6.6 | BURY | BURY | KEARSLEY | 380863 | 410807 | 400 | 4.5726 | 8.5668 | 12.7038 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.2958 | Connections Reform
BUSHELL ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353809 | 430094 | 400 | 4.5726 | 10.4706 | 27 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.8954 | Connections Reform
CAMPBELL ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372937 | 406428 | 630 | 12.0031 | 0 | 9.2979 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 5.9733 | Connections Reform
CANNON ST | 6.6 | RED BANK | RED BANK | WHITEGATE | 384064 | 398635 | 400 | 4.5726 | 4.7518 | 27.7619 | 0.33792 | 0.054807 | 0.039988 | 0.33792 | 0.16545 | 1.3982 | Connections Reform
CAPONTREE | 11 | CARLISLE | CARLISLE | HARKER | 352906 | 559671 | 400 | 7.621 | 14.8326 | 17.1696 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
CARLETON | 11 | EGREMONT | EGREMONT | HARKER | 308796 | 498305 | 630 | 12.0031 | 2.672 | 5.172 | 7.534 | 3.1754 | 2.3269 | 5.172 | 8.424 | 5.5206 | Connections Reform
CARR ST | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376984 | 401329 | 400 | 7.621 | 0 | 14.1419 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
CASTLETON | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 388461 | 411290 | 630 | 7.2019 | 6.8857 | 11.5227 | 20.6955 | 3.3565 | 2.449 | 11.5227 | 2.09 | 9.5109 | Connections Reform
CATTERALL WATERWORKS | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349381 | 442178 | 400 | 4.5726 | 0 | 0 | 9.3899 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
CECIL ST | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 331301 | 437023 | 630 | 7.2019 | 9.5316 | 14.7216 | 31.2088 | 16.4444 | 11.9983 | 14.7216 | 12.1148 | 12.9781 | Connections Reform
CENTRAL MANCHESTER | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 384852 | 397718 | 630 | 7.2019 | 0 | 9.191 | 11.2179 | 1.9575 | 1.4344 | 9.191 | 1.4344 | 0 | Connections Reform
CHADDERTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389161 | 403872 | 400 | 4.5726 | 4.4217 | 4.4217 | 25.2563 | 4.0962 | 2.9887 | 4.4217 | 1.3649 | 0 | Connections Reform
CHAMBERHALL | 6.6 | BURY | BURY | KEARSLEY | 380280 | 411215 | 600 | 6.8589 | 3.4134 | 8.7334 | 11.2179 | 1.9575 | 1.4344 | 8.7334 | 1.4344 | 8.4761 | Connections Reform
CHAPEL WHARF | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383499 | 398634 | 630 | 7.2019 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
CHASSEN RD | 6.6 | BARTON | BARTON | CARRINGTON | 375542 | 394453 | 630 | 7.2019 | 1.3081 | 12.2081 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
CHATSWORTH ST | 11 | BARROW & SANDGATE | BARROW | HARKER | 319188 | 470003 | 800 | 15.242 | 8.7008 | 16.1008 | 30.2519 | 10.1582 | 7.3009 | 16.1008 | 7.3076 | 14.6753 | Connections Reform
CHEADLE HEATH | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 387062 | 389054 | 630 | 7.2019 | 0 | 2.7549 | 21.3975 | 10.7809 | 7.8661 | 2.7549 | 8.0328 | 8.3048 | Connections Reform
CHEADLE HULME | 11 | ADSWOOD | ADSWOOD | BREDBURY | 387386 | 386308 | 630 | 12.0031 | 3.7979 | 8.4349 | 31.0275 | 12.9142 | 9.2817 | 8.4349 | 9.2691 | 12.9036 | Connections Reform
CHEETHAM HILL | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 383606 | 402218 | 400 | 4.5726 | 2.1036 | 2.1036 | 22.1641 | 15.1749 | 11.072 | 2.1036 | 11.1639 | 2.7039 | Connections Reform
CHESTER RD T11 & T12 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381030 | 396165 | 630 | 7.2019 | 0 | 2.9865 | 25.839 | 9.5488 | 6.9671 | 2.9865 | 5.9831 | 2.9543 | Connections Reform
CHESTER RD T13 | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 381040 | 396175 | 630 | 7.2019 | 8.0071 | 13.0635 | 18.5639 | 18.5639 | 17.1186 | 13.0635 | 17.154 | 12.6129 | Connections Reform
CHORLEY SOUTH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358658 | 417041 | 800 | 15.242 | 0 | 0 | 24.2238 | 13.2954 | 9.5557 | 0 | 5.1053 | 5.0492 | Connections Reform
CHORLTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 381411 | 393754 | 400 | 4.5726 | 5.4598 | 11.4598 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 9.12 | Connections Reform
CHURCH | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374687 | 428919 | 800 | 9.1452 | 5.8561 | 12.6561 | 13.9117 | 13.9117 | 13.9117 | 12.6561 | 7.0436 | 11.2916 | Connections Reform
CIRCLE SQ | 6.6 | Longsight | LONGSIGHT | BREDBURY | 384365 | 397285 | 630 | 7.2 | 0 | 18.789 | 24.2035 | 11.3284 | 8.2655 | 18.789
CLARENDON RD | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369051 | 429883 | 400 | 4.5726 | 5.0176 | 9.6546 | 30.8503 | 12.6558 | 9.2341 | 9.6546 | 2.9125 | 3.9899 | Connections Reform
CLAUGHTON | 11 | LANCASTER | LANCASTER | HEYSHAM | 355872 | 466268 | 630 | 12.0031 | 1.1244 | 4.6507 | 8.1667 | 1.9575 | 1.4344 | 4.6507 | 1.5151 | 3.7068 | Connections Reform
BLACKBURN RD CLAYTON | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 374632 | 430529 | 630 | 7.2019 | 11.3975 | 19.0775 | 25.3708 | 10.7513 | 7.8444 | 19.0775 | 7.0436 | 19.3058 | Connections Reform
CLEVELEYS | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 332286 | 443104 | 630 | 7.2019 | 5.7073 | 9.2073 | 11.2179 | 1.9575 | 1.4344 | 9.2073 | 1.4344 | 7.8631 | Connections Reform
CLIFTON JUNCTION | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 379289 | 403073 | 630 | 12.0031 | 0 | 9.0006 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 4.7605 | Connections Reform
CLOVER HILL | 6.6 | NELSON | NELSON | PADIHAM | 386638 | 437064 | 630 | 7.2019 | 10.0813 | 19.5967 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
COG LANE | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 382462 | 432232 | 800 | 9.1452 | 5.2261 | 15.651 | 43.2277 | 8.5663 | 6.2502 | 15.651 | 1.845 | 13.1837 | Connections Reform
CONISTON | 11 | ULVERSTON | ULVERSTON | HARKER | 329874 | 497641 | 400 | 7.621 | 0 | 1.0476 | 4.6591 | 4.6591 | 4.6591 | 1.0476 | 4.8516 | 1.4303 | Connections Reform
COPSE RD | 6.6 | THORNTON | THORNTON | STANAH | 333013 | 446934 | 630 | 7.2019 | 6.5778 | 8.2148 | 22.6752 | 5.0099 | 3.6554 | 8.2148 | 2.296 | 3.1319 | Connections Reform
COX GREEN | 11 | BOLTON | BOLTON | KEARSLEY | 371893 | 413641 | 630 | 12.0031 | 5.7689 | 10.0689 | 11.2179 | 1.9575 | 1.4344 | 10.0689 | 1.4344 | 8.1583 | Connections Reform
CRAGGS ROW | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 353740 | 430080 | 630 | 7.2019 | 5.2644 | 9.4044 | 11.2179 | 1.9575 | 1.4344 | 9.4044 | 1.4344 | 9.0804 | Connections Reform
CROWN LANE | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 362706 | 410859 | 400 | 7.621 | 2.6566 | 7.2936 | 32.1918 | 7.0151 | 5.0419 | 7.2936 | 0.088852 | 0 | Connections Reform
CULCHETH | 11 | GOLBORNE | GOLBORNE | BOLD | 365430 | 395366 | 400 | 7.621 | 0 | 0 | 13.617 | 9.447 | 6.9226 | 0 | 0 | 0 | N/A
CUTACRE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 369848 | 404515 | 630 | 12.0031 | 0 | 6.4383 | 7 | 1.9575 | 1.4344 | 6.4383 | 1.4344 | 7 | Connections Reform
DALTON | 11 | ULVERSTON | ULVERSTON | HARKER | 323582 | 474255 | 400 | 7.621 | 4.6623 | 12.1423 | 29.413 | 15.5103 | 11.1475 | 12.1423 | 11.6712 | 8.928 | Connections Reform
DEANSGATE | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383463 | 398149 | 630 | 7.2019 | 0 | 10.4408 | 30.1444 | 12.3592 | 9.0176 | 10.4408 | 9.1618 | 11.3246 | Connections Reform
DENTON EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 392394 | 395626 | 630 | 7.2019 | 10.5529 | 15.1899 | 2.3359 | 0.40761 | 0.29869 | 2.3359 | 1.4344 | 11.2179 | Connections Reform
DENTON WEST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390380 | 395565 | 400 | 4.5726 | 6.1929 | 10.8299 | 2.3359 | 0.40761 | 0.29869 | 2.3359 | 1.4344 | 11.2179 | Connections Reform
DICKINSON ST T11 & T12 | 6.6 | Bloom St | BLOOM ST | SOUTH MANCHESTER | 384109 | 397722 | 800 | 9.1452 | 0 | 14.0154 | 36.9183 | 12.5071 | 9.1255 | 14.0154
DICKINSON ST T13 | 6.6 | Stuart Street | STUART ST | STALYBRIDGE | 384109 | 397722 | 800 | 9.1452 | 9.9138 | 23.9138 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 9.5067 | 5.4068 | Connections Reform
DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384792 | 391153 | 630 | 7.2019 | 8.2941 | 12.9311 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 11.2179 | Connections Reform
DODGSON RD | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 355190 | 430397 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
DOUGLAS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352220 | 429932 | 400 | 4.5726 | 8.1058 | 14.7658 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
DROYLSDEN EAST | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 390532 | 398053 | 630 | 7.2019 | 7.8107 | 12.4507 | 2.3359 | 0.40761 | 0.29869 | 2.3359 | 1.4344 | 9.4097 | Connections Reform
DUKINFIELD | 6.6 | HYDE | HYDE | STALYBRIDGE | 394372 | 396438 | 400 | 4.5726 | 10.0185 | 16.0209 | 22.3734 | 3.7287 | 2.7205 | 16.0209 | 2.6715 | 15.6217 | Connections Reform
DUMERS LANE | 11 | BURY | BURY | KEARSLEY | 380057 | 408141 | 400 | 7.621 | 4.415 | 10.915 | 11.2179 | 1.9575 | 1.4344 | 10.915 | 1.4344 | 7.2779 | Connections Reform
DUMPLINGTON | 11 | BARTON | BARTON | CARRINGTON | 376770 | 397157 | 800 | 15.242 | 12.7218 | 14.1218 | 7.0057 | 1.1534 | 0.829 | 7.0057 | 0.99981 | 8.4492 | Connections Reform
EASTLANDS | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386458 | 398693 | 800 | 9.1452 | 1.0633 | 5.7003 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
EASTON | 11 | - | - | HARKER | 343201 | 571738 | 800 | 15.242 | 0 | 0 | 2.435 | 2.435 | 2.435 | 0 | 2.8786 | 0 | Connections Reform
EGREMONT | 11 | EGREMONT | EGREMONT | HARKER | 301070 | 513074 | 400 | 7.621 | 0.93043 | 3.4304 | 18.1974 | 3.1754 | 2.3269 | 3.4304 | 12.6319 | 4.995 | Connections Reform
EMBLETON | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 315767 | 529389 | 630 | 12.0031 | 3.9629 | 14.9629 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
EXCHANGE ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369100 | 423028 | 800 | 9.1452 | 3.3077 | 6.8077 | 22.6154 | 3.9463 | 2.8918 | 6.8077 | 0 | 0 | Connections Reform
FAILSWORTH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 389631 | 401496 | 400 | 4.5726 | 4.4217 | 4.4217 | 28.4034 | 8.689 | 6.3672 | 4.4217 | 1.3649 | 0 | Connections Reform
FALLOWFIELD | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 385608 | 393881 | 400 | 4.5726 | 1.0806 | 5.7176 | 11.048 | 1.9575 | 1.4344 | 5.7176 | 1.4344 | 11.2006 | Connections Reform
FARNWORTH | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373726 | 405532 | 800 | 15.242 | 0 | 10.9049 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
FENISCOWLES | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 364660 | 425120 | 630 | 7.2019 | 2.9228 | 15.2228 | 18.6096 | 3.9463 | 2.8918 | 15.2228 | 0 | 0 | Connections Reform
FERODO | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 405720 | 381338 | 630 | 12.0031 | 3.2302 | 14.1902 | 29.298 | 15.7507 | 11.3204 | 14.1902 | 11.2192 | 5.6473 | Connections Reform
FLAT LANE | 11 | PADIHAM | NELSON | PADIHAM | 383248 | 456995 | 630 | 12.0031 | 0.5055 | 6.0055 | 10.839 | 10.839 | 10.839 | 6.0055 | 11.0501 | 4.4257 | Connections Reform
FREDERICK RD | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381697 | 399348 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
FUSEHILL | 11 | CARLISLE | CARLISLE | HARKER | 341042 | 555452 | 400 | 7.621 | 6.0103 | 12.5103 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
GALE | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 389570 | 414943 | 400 | 4.5726 | 13.0988 | 17.7358 | 29.2281 | 12.1935 | 8.8967 | 17.7358 | 8.6697 | 0 | Connections Reform
GARSTANG | 6.6 | THORNTON | THORNTON | STANAH | 348319 | 445221 | 630 | 7.2019 | 3.2105 | 3.2105 | 13.8416 | 12.5579 | 9.2023 | 3.2105 | 9.0987 | 0.2593 | Connections Reform
GATLEY | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384242 | 388388 | 400 | 4.5726 | 2.6936 | 13.1936 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | Connections Reform
GIDLOW | 6.6 | WIGAN | WIGAN | KIRKBY | 357620 | 406662 | 400 | 4.5726 | 4.0886 | 8.7256 | 30.601 | 13.1829 | 9.6186 | 8.7256 | 8.9257 | 9.6892 | Connections Reform
GILLSROW | 11 | PENRITH & SHAP | PENRITH | HUTTON | 337117 | 526444 | 630 | 12.0031 | 0.43687 | 2.6369 | 7.5878 | 7.5878 | 7.5878 | 2.6369 | 7.4769 | 2.881 | Connections Reform
GLAXO | 11 | ULVERSTON | ULVERSTON | HARKER | 330458 | 477825 | 400 | 7.621 | 8.8403 | 21.324 | 10.3246 | 1.6999 | 1.2217 | 10.3246 | 1.4212 | 12.0107 | Connections Reform
GLOSSOP | 11 | HYDE | HYDE | STALYBRIDGE | 402300 | 394074 | 630 | 12.0031 | 8.494 | 13.131 | 30.683 | 5.6765 | 4.1597 | 13.131 | 5.4751 | 12.055 | Connections Reform
GOLBORNE T11 & T12 | 11 | GOLBORNE | GOLBORNE | BOLD | 360621 | 397766 | 800 | 15.242 | 10.1109 | 15.6109 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
GOWHOLE | 11 | NEW MILLS | NEW MILLS | STALYBRIDGE | 401104 | 383846 | 400 | 7.621 | 6.8593 | 6.8593 | 24.3991 | 8.8889 | 6.3887 | 6.8593 | 7.0494 | 5.6473 | Connections Reform
GRANE RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378312 | 422726 | 400 | 4.5726 | 9.9582 | 15.0582 | 25.0372 | 5.8842 | 4.2933 | 15.0582 | 5.885 | 14.3872 | Connections Reform
GRANGE | 11 | ULVERSTON | ULVERSTON | HARKER | 340240 | 478314 | 400 | 7.621 | 6.0312 | 12.0312 | 20.9969 | 20.9969 | 19.3947 | 12.0312 | 19.5311 | 10.7263 | Connections Reform
GREAT HARWOOD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373765 | 431955 | 630 | 7.2019 | 10.3489 | 18.4689 | 17.7841 | 3.4408 | 2.5105 | 17.7841 | 1.1085 | 9.368 | Connections Reform
GREEN LANE (ALTRINCHAM) | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 378744 | 387772 | 400 | 7.621 | 7.3126 | 11.9496 | 31.6854 | 15.6982 | 11.2826 | 11.9496 | 11.1508 | 10.8283 | Connections Reform
GREEN LANE (HAZEL GROVE) | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 391570 | 387132 | 400 | 7.621 | 2.169 | 6.806 | 31.5238 | 9.049 | 6.5037 | 6.806 | 5.6166 | 0.45951 | Connections Reform
GREEN ST T11 | 6.6 | WIGAN | WIGAN | KIRKBY | 358235 | 404898 | 630 | 7.2019 | 1.9689 | 5.9689 | 19.3178 | 19.3178 | 17.6736 | 5.9689 | 4.1968 | 3.8848 | Connections Reform
GREEN ST T12 & T13 | 6.6 | WIGAN | WIGAN | KIRKBY | 358225 | 404888 | 630 | 7.2019 | 2.5388 | 8.0788 | 31.2798 | 8.8882 | 6.4851 | 8.0788 | 5.7981 | 10.2071 | Connections Reform
GREENFIELD | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 399322 | 404583 | 800 | 15.242 | 13.4682 | 17.9682 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
GREENHILL | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 393262 | 404755 | 400 | 4.5726 | 11.3681 | 11.3681 | 61.8488 | 10.1589 | 7.4122 | 11.3681 | 6.8407 | 4.6017 | Connections Reform
GRIFFIN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 367171 | 427130 | 800 | 9.1452 | 8.9927 | 13.6327 | 22.6154 | 3.9463 | 2.8918 | 13.6327 | 0 | 0 | Connections Reform
HADFIELD | 11 | HYDE | HYDE | STALYBRIDGE | 401790 | 395876 | 400 | 7.621 | 10.7386 | 17.4656 | 7.7213 | 1.2713 | 0.91368 | 7.7213 | 0.83754 | 7.0779 | Connections Reform
HALL CROSS | 6.6 | PEEL | PEEL | PENWORTHAM | 342288 | 430650 | 630 | 7.2019 | 1.943 | 2.0211 | 21.5498 | 10.5776 | 7.7177 | 2.0211 | 0 | 0 | Connections Reform
HANDFORTH | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385958 | 383397 | 400 | 7.621 | 7.1088 | 11.7458 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | Connections Reform
HANGING BRIDGE | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 346186 | 417486 | 630 | 12.0031 | 0 | 0 | 10.8309 | 10.8309 | 10.8309 | 0 | 5.1053 | 5.1053 | Connections Reform
HAREHOLME | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 382535 | 422283 | 800 | 9.1452 | 7.9024 | 12.5394 | 29.3567 | 12.3091 | 8.9811 | 12.5394 | 9.5452 | 9.9239 | Connections Reform
HARPURHEY | 6.6 | RED BANK | RED BANK | WHITEGATE | 385907 | 402469 | 400 | 4.5726 | 11.3825 | 16.0225 | 30.0164 | 12.4866 | 9.1105 | 16.0225 | 9.1946 | 15.552 | Connections Reform
HARWOOD | 11 | BOLTON | BOLTON | KEARSLEY | 374043 | 410941 | 400 | 7.621 | 1.2154 | 5.5154 | 11.2179 | 1.9575 | 1.4344 | 5.5154 | 1.4344 | 7.187 | Connections Reform
HATTERSLEY | 11 | HYDE | HYDE | STALYBRIDGE | 398419 | 395120 | 800 | 15.242 | 0 | 0 | 14.7253 | 4.7231 | 3.3946 | 0 | 3.4214 | 6.4802 | Connections Reform
HAVERTHWAITE | 11 | ULVERSTON | ULVERSTON | HARKER | 334234 | 483827 | 630 | 12.0031 | 4.2976 | 6.7976 | 13.1381 | 13.1381 | 13.1381 | 6.7976 | 13.0026 | 6.7952 | Connections Reform
HAWK GREEN | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395915 | 387138 | 630 | 12.0031 | 12.4311 | 16.9311 | 29.6601 | 16.6339 | 11.9551 | 16.9311 | 12.0132 | 15.4515 | Connections Reform
HAYDOCK | 11 | GOLBORNE | GOLBORNE | BOLD | 357489 | 397336 | 630 | 12.0031 | 0.873 | 9.4781 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | N/A
HDA NO1 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301743 | 524532 | 400 | 7.621 | 13.8056 | 20.0256 | 2.7336 | 0.45007 | 0.32347 | 2.7336 | 0 | 0 | Connections Reform
HDA NO2 | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301429 | 525527 | 630 | 12.0031 | 13.8056 | 20.0256 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
HEADY HILL | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 384370 | 410583 | 400 | 4.5726 | 6.0872 | 9.5872 | 23.2195 | 9.7233 | 7.0944 | 9.5872 | 7.0425 | 7.7035 | Connections Reform
HEAP BRIDGE | 6.6 | BURY | BURY | KEARSLEY | 382793 | 410428 | 400 | 4.5726 | 3.658 | 3.658 | 8.3721 | 1.9575 | 1.4344 | 3.658 | 1.4344 | 2.695 | Connections Reform
HEASANDFORD | 6.6 | BURNLEY | BURNLEY | ROCHDALE | 385349 | 433821 | 400 | 4.5726 | 9.2961 | 18.5061 | 29.0742 | 8.8695 | 6.4714 | 18.5061 | 0 | 0 | Connections Reform
HEATON MOOR | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 387623 | 391345 | 630 | 7.2019 | 1.5589 | 1.5589 | 30.021 | 9.5831 | 6.9921 | 1.5589 | 7.1221 | 0 | Connections Reform
HEATON NORRIS | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 388860 | 391967 | 400 | 4.5726 | 0.6913 | 1.5589 | 24.0291 | 4.7167 | 3.4414 | 1.5589 | 3.0681 | 0 | Connections Reform
HELWITH BRIDGE | 11 | PADIHAM | PADIHAM | PADIHAM | 381025 | 469428 | 630 | 12.0031 | 0.65207 | 8.6521 | 12.4038 | 12.4038 | 12.4038 | 8.6521 | 13.2972 | 8.3367 | Connections Reform
HENSINGHAM | 11 | EGREMONT | EGREMONT | HARKER | 298465 | 517239 | 630 | 12.0031 | 14.0646 | 18.2016 | 18.1974 | 3.1754 | 2.3269 | 18.1974 | 9.101 | 17.1039 | Connections Reform
HEYROD | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397310 | 399981 | 600 | 6.8589 | 10.0114 | 14.6484 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
HEYSIDE | 6.6 | ROYTON | ROYTON | WHITEGATE | 393433 | 407129 | 400 | 4.5726 | 5.3712 | 13.9204 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
HEYWOOD | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 385429 | 410369 | 630 | 7.2019 | 1.3671 | 3.87 | 15.9242 | 2.5827 | 1.8844 | 3.87 | 1.2885 | 0 | Connections Reform
HIGHER MILL | 6.6 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 385731 | 388090 | 400 | 4.5726 | 5.2383 | 12.7383 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | Connections Reform
HIGHER WALTON | 11 | LEYLAND | LEYLAND | PENWORTHAM | 358020 | 427270 | 400 | 7.621 | 6.7928 | 11.4298 | 23.2983 | 5.4147 | 3.8917 | 11.4298 | 3.7037 | 4.126 | Connections Reform
HILL TOP T11 & T12 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373466 | 403748 | 400 | 7.621 | 0 | 7.345 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
HILL TOP T13 | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 373476 | 403758 | 400 | 7.621 | 0 | 0.52202 | 6.5049 | 1.9575 | 1.4344 | 0.52202 | 1.4344 | 0.95096 | Connections Reform
HINDLEY GREEN | 11 | ATHERTON | ATHERTON | KEARSLEY | 363389 | 403254 | 630 | 12.0031 | 10.2956 | 16.8357 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 0 | Connections Reform
HOLLINWOOD | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 390287 | 402592 | 630 | 7.2019 | 4.4217 | 4.4217 | 27.1006 | 7.3527 | 5.3647 | 4.4217 | 1.3649 | 0 | Connections Reform
HOLME RD | 11 | RIBBLE | RIBBLE | PENWORTHAM | 352311 | 429141 | 400 | 7.621 | 6.9476 | 11.0846 | 11.2179 | 1.9575 | 1.4344 | 11.0846 | 1.4344 | 11.2179 | Connections Reform
HOLT ST | 11 | BURY | BURY | KEARSLEY | 378620 | 416362 | 630 | 12.0031 | 5.1794 | 8.6794 | 11.2179 | 1.9575 | 1.4344 | 8.6794 | 1.4344 | 6.5258 | Connections Reform
HURST | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 394658 | 400360 | 630 | 7.2019 | 4.1207 | 7.6207 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
HUTTON END | 11 | PENRITH & SHAP | PENRITH | HUTTON | 345810 | 538827 | 630 | 12.0031 | 10.2795 | 12.6267 | 20.6196 | 20.6196 | 16.5025 | 12.6267 | 17.2503 | 13.3736 | Connections Reform
HYDE | 6.6 | HYDE | HYDE | STALYBRIDGE | 395215 | 395126 | 630 | 7.2019 | 6.3973 | 11.0343 | 31.6572 | 5.6765 | 4.1597 | 11.0343 | 5.4751 | 11.4433 | Connections Reform
HYNDBURN RD | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 375688 | 428877 | 800 | 9.1452 | 4.8839 | 17.1839 | 29.3443 | 13.5687 | 9.9001 | 17.1839 | 7.0436 | 17.6125 | Connections Reform
INDIA ST | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369485 | 421865 | 400 | 4.5726 | 9.4116 | 18.8949 | 22.6154 | 3.9463 | 2.8918 | 18.8949 | 0 | 0 | Connections Reform
INGLETON | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 368913 | 472337 | 630 | 12.0031 | 2.0512 | 10.0512 | 12.4695 | 12.4695 | 12.4695 | 10.0512 | 0 | 0 | Connections Reform
IRLAM | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 371680 | 393360 | 1250 | 14.2894 | 2.926 | 7.066 | 11.2179 | 1.9575 | 1.4344 | 7.066 | 1.4344 | 4.4053 | Connections Reform
JAMES ST | 11 | CARLISLE | CARLISLE | HARKER | 340034 | 555418 | 630 | 12.0031 | 3.8704 | 8.0074 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
KAY ST | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 373863 | 427594 | 630 | 7.2019 | 13.9136 | 18.0506 | 29.0556 | 13.3573 | 9.7459 | 18.0506 | 7.0436 | 16.5205 | Connections Reform
KENDAL | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351915 | 491858 | 400 | 7.621 | 4.7438 | 8.7438 | 28.4174 | 9.0533 | 6.5068 | 8.7438 | 0 | 0 | Connections Reform
KESWICK | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 327022 | 523784 | 400 | 7.621 | 5.6848 | 8.1848 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
KINGSWAY | 11 | BELFIELD | BELFIELD | ROCHDALE | 391636 | 411724 | 630 | 12.0031 | 23.2239 | 30.4611 | 47.0319 | 8.0935 | 5.817 | 30.4611 | 1.6009 | 0 | Connections Reform
KINKRY HILL | 11 | - | - | HARKER | 350800 | 575111 | 800 | 15.242 | 0.74632 | 2.2463 | 3.1382 | 3.1382 | 3.1382 | 2.2463 | 3.1954 | 2.3112 | Connections Reform
KIRKBY LONSDALE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 359833 | 478813 | 400 | 7.621 | 3.4129 | 7.4129 | 13.3001 | 13.3001 | 13.3001 | 7.4129 | 0 | 0 | Connections Reform
KIRKBY MOOR | 11 | ULVERSTON | ULVERSTON | HARKER | 326099 | 483011 | 1250 | 23.8157 | 2.4788 | 5.9788 | 2.5787 | 2.5787 | 2.5787 | 2.5787 | 2.8987 | 2.8987 | Connections Reform
KIRKBY STEPHEN | 11 | PENRITH & SHAP | PENRITH | HUTTON | 376579 | 509136 | 800 | 15.242 | 9.384 | 11.884 | 18.838 | 18.838 | 18.838 | 11.884 | 19.5904 | 10.2783 | Connections Reform
KIRKBY THORE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 364439 | 526672 | 630 | 12.0031 | 4.2527 | 12.6267 | 21.1232 | 21.1232 | 17.6006 | 12.6267 | 18.6543 | 13.2545 | Connections Reform
KIRKHALL LANE | 11 | ATHERTON | ATHERTON | KEARSLEY | 365510 | 401069 | 400 | 7.621 | 5.7135 | 8.0635 | 21.2353 | 11.3849 | 8.1825 | 8.0635 | 8.0695 | 0 | Connections Reform
KITT GREEN | 6.6 | ORRELL | ORRELL | KIRKBY | 354934 | 405497 | 400 | 4.5726 | 3.6164 | 12.3145 | 30.9806 | 13.0859 | 9.5478 | 12.3145 | 9.0797 | 10.8837 | Connections Reform
KNOTT MILL | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 383136 | 397725 | 800 | 9.1452 | 0 | 0 | 29.3481 | 6.9391 | 5.0629 | 0 | 4.9077 | 0 | Connections Reform
LAMBERHEAD | 6.6 | ORRELL | ORRELL | KIRKBY | 355516 | 404030 | 630 | 7.2019 | 3.6164 | 13.56 | 22.7737 | 9.9371 | 7.2504 | 13.56 | 7.0795 | 15.6051 | Connections Reform
LANCASTER | 11 | LANCASTER | LANCASTER | HEYSHAM | 348644 | 463628 | 630 | 12.0031 | 5.0571 | 9.1941 | 11.2179 | 1.9575 | 1.4344 | 9.1941 | 1.5151 | 5.0572 | Connections Reform
LANGLEY | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 386421 | 406330 | 400 | 7.621 | 3.147 | 4.4217 | 31.2857 | 8.689 | 6.3672 | 4.4217 | 1.3649 | 0 | Connections Reform
LANGROYD RD | 6.6 | NELSON | NELSON | PADIHAM | 389077 | 440584 | 400 | 4.5726 | 10.0813 | 14.9572 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
LEIGH | 11 | ATHERTON | ATHERTON | KEARSLEY | 365863 | 399907 | 800 | 15.242 | 3.3864 | 11.3864 | 19.4357 | 19.4357 | 19.4357 | 11.3864 | 19.6186 | 0 | Connections Reform
LEVENSHULME | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 387494 | 394155 | 400 | 4.5726 | 0 | 5.3556 | 24.6755 | 14.0815 | 10.2742 | 5.3556 | 10.1941 | 6.1719 | Connections Reform
LEYLAND NATIONAL | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 301973 | 525948 | 400 | 7.621 | 14.174 | 22.3127 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Connections Reform
LITTLE HULTON | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 372024 | 403826 | 630 | 12.0031 | 0 | 5.7349 | 7 | 1.9575 | 1.4344 | 5.7349 | 1.4344 | 4.4466 | Connections Reform
LITTLE SALKELD | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356221 | 537513 | 400 | 7.621 | 2.7649 | 5.0511 | 15.691 | 15.691 | 15.691 | 5.0511 | 16.5605 | 4.0762 | Connections Reform
LITTLEBOROUGH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 393221 | 416124 | 400 | 4.5726 | 3.997 | 7.497 | 24.3866 | 10.052 | 7.3342 | 7.497 | 6.9929 | 0 | Connections Reform
LONGFORD BRIDGE | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380056 | 395083 | 800 | 9.1452 | 6.3367 | 10.9737 | 29.2493 | 7.6219 | 5.5611 | 10.9737 | 5.7031 | 10.4658 | Connections Reform
LONGRIDGE | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 360581 | 437001 | 400 | 4.5726 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
LONGSIGHT | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385535 | 396037 | 400 | 4.5726 | 0 | 5.7567 | 27.811 | 5.3639 | 3.9136 | 5.7567 | 2.8907 | 9.1882 | Connections Reform
LOSTOCK | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365293 | 409079 | 800 | 15.242 | 4.4337 | 10.4337 | 36.6295 | 6.0308 | 4.3344 | 10.4337 | 0.088852 | 0 | Connections Reform
LOWER DARWEN | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369695 | 424981 | 800 | 9.1452 | 8.4199 | 17.449 | 22.6154 | 3.9463 | 2.8918 | 17.449 | 0 | 0 | Connections Reform
LYONS RD | 6.6 | BARTON | BARTON | CARRINGTON | 378253 | 397241 | 400 | 4.5726 | 0 | 0.15636 | 11.2179 | 1.9575 | 1.4344 | 0.15636 | 1.4344 | 10.6576 | Connections Reform
MANCHESTER UNIVERSITY | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384762 | 396769 | 800 | 9.1452 | 0 | 0.32011 | 32.9592 | 10.2263 | 7.4614 | 0.32011 | 7.4513 | 1.5496 | Connections Reform
MARPLE | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 395671 | 388643 | 630 | 12.0031 | 0 | 0 | 6.0932 | 6.0932 | 6.0932 | 0 | 7.1061 | 0 | Connections Reform
MARTON | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 333341 | 433485 | 400 | 4.5726 | 8.289 | 14.295 | 24.787 | 8.7241 | 6.3653 | 14.295 | 6.5522 | 14.5624 | Connections Reform
MARYPORT | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 303716 | 535313 | 630 | 12.0031 | 7.8843 | 18.2883 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
MEDIPARK | 11 | ALTRINCHAM | ALTRINCHAM | CARRINGTON | 380478 | 387812 | 630 | 12.0028 | 24.7276 | 33.8649 | 38.7798 | 10.3202 | 7.4174 | 33.8649
MELLING | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 360144 | 471643 | 630 | 12.0031 | 1.8254 | 3.8254 | 6.5282 | 6.5282 | 6.5282 | 3.8254 | 0 | 0 | Connections Reform
MERESIDE | 6.6 | PEEL | PEEL | PENWORTHAM | 334431 | 434843 | 630 | 7.2019 | 2.0211 | 2.0211 | 21.5498 | 13.0659 | 9.5332 | 2.0211 | 0 | 0 | Connections Reform
MIDDLETON JUNCTION | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 388606 | 405292 | 630 | 12.0031 | 4.0034 | 4.4217 | 26.2779 | 4.3265 | 3.1095 | 4.4217 | 1.3649 | 0 | Connections Reform
MIDWAY | 11 | EGREMONT | EGREMONT | HARKER | 304525 | 501993 | 630 | 12.0031 | 9.6272 | 12.3313 | 17.9247 | 3.1754 | 2.3269 | 12.3313 | 18.0835 | 11.4916 | Connections Reform
MILNROW | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 392351 | 413056 | 400 | 4.5726 | 12.3358 | 16.9758 | 29.2996 | 10.5845 | 7.7228 | 16.9758 | 7.4802 | 14.0754 | Connections Reform
MINTSFEET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351827 | 494315 | 400 | 7.621 | 5.1619 | 11.1619 | 14.7607 | 2.4302 | 1.7467 | 11.1619 | 0 | 0 | Connections Reform
MONSALL | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 386332 | 401003 | 630 | 7.2019 | 4.2972 | 13.7972 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 0 | Connections Reform
MONTON | 6.6 | BARTON | BARTON | CARRINGTON | 376321 | 399494 | 400 | 4.5726 | 4.5488 | 8.0488 | 11.2179 | 1.9575 | 1.4344 | 8.0488 | 1.4344 | 5.0297 | Connections Reform
MOORSIDE | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 349331 | 435746 | 630 | 7.2019 | 3.3792 | 6.8792 | 11.2179 | 1.9575 | 1.4344 | 6.8792 | 1.4344 | 8.9507 | Connections Reform
MORTON PARK | 11 | CARLISLE | CARLISLE | HARKER | 337826 | 553939 | 1250 | 23.8157 | 6.7947 | 11.5919 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0.31765 | 2.6844 | Connections Reform
MOSLEY RD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 379058 | 396289 | 630 | 7.2019 | 3.6833 | 6.7022 | 22.3017 | 8.7434 | 6.3795 | 6.7022 | 5.8695 | 0 | Connections Reform
MOSS LANE | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 380858 | 405856 | 400 | 7.621 | 0 | 5.6847 | 7 | 1.9575 | 1.4344 | 5.6847 | 1.4344 | 3.7702 | Connections Reform
MOSS NOOK PRIMARY | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384084 | 385010 | 800 | 15.242 | 7.6878 | 22.3333 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 5.768 | Connections Reform
MOSS SIDE (Leyland) | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352170 | 422970 | 400 | 7.621 | 0 | 2.7523 | 27.2809 | 12.8142 | 9.2098 | 2.7523 | 9.1199 | 4.5253 | Connections Reform
MOSS SIDE (Longsight) | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 384007 | 395893 | 400 | 4.5726 | 0 | 2.0451 | 33.5948 | 10.1241 | 7.3868 | 2.0451 | 7.5673 | 1.6732 | Connections Reform
MOSSLEY | 11 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 397437 | 401979 | 400 | 7.621 | 10.6641 | 15.3011 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
MOUNT ST | 6.6 | BARTON | BARTON | CARRINGTON | 376250 | 397574 | 400 | 4.5726 | 0.98298 | 5.6199 | 11.2179 | 1.9575 | 1.4344 | 5.6199 | 1.4344 | 8.7054 | Connections Reform
MUSGRAVE RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 370045 | 409863 | 800 | 9.1452 | 8.3515 | 13.9715 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
NELSON | 6.6 | NELSON | NELSON | PADIHAM | 386020 | 438507 | 400 | 4.5726 | 5.0887 | 9.2287 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
NEW MOSTON | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388333 | 402657 | 630 | 7.2019 | 4.4217 | 4.4217 | 29.7533 | 8.689 | 6.3672 | 4.4217 | 1.3649 | 0 | Connections Reform
NEWBIGGIN ON LUNE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 369770 | 505803 | 800 | 15.242 | 0 | 1.4628 | 3.2149 | 3.2149 | 3.2149 | 1.4628 | 3.8322 | 2.0546 | Connections Reform
NEWBY | 11 | PENRITH & SHAP | PENRITH | HUTTON | 360520 | 521151 | 400 | 7.621 | 0.43921 | 7.4392 | 14.6189 | 14.6189 | 14.6189 | 7.4392 | 15.0523 | 7.0631 | Connections Reform
NEWTON | 11 | HYDE | HYDE | STALYBRIDGE | 396385 | 396464 | 400 | 7.621 | 9.2794 | 14.2794 | 18.4853 | 5.6765 | 4.1597 | 14.2794 | 1.511 | 1.511 | Connections Reform
NEWTON HEATH | 6.6 | CHADDERTON | CHADDERTON | WHITEGATE | 388030 | 400511 | 400 | 4.5726 | 1.0946 | 1.0946 | 12.0002 | 8.689 | 6.3672 | 1.0946 | 1.3649 | 0 | Connections Reform
NEWTON LE WILLOWS | 11 | GOLBORNE | GOLBORNE | BOLD | 357891 | 395944 | 630 | 12.0031 | 5.9021 | 10.0391 | 26.6116 | 9.447 | 6.9226 | 10.0391 | 0 | 0 | N/A
NEWTONGATE T11 & T12 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 1.3123 | 5.3123 | 21.1232 | 6.4152 | 4.6108 | 5.3123 | 3.841 | 8.6565 | Connections Reform
NEWTONGATE T13 | 11 | PENRITH & SHAP | PENRITH | HUTTON | 349973 | 530340 | 630 | 12.0031 | 1.0047 | 5.7547 | 19.7335 | 19.7335 | 19.3338 | 5.7547 | 14.4183 | 10.2752 | Connections Reform
NORBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331831 | 441463 | 400 | 4.5726 | 17.2283 | 23.5559 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
NORBURY | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392447 | 385492 | 400 | 7.621 | 9.6773 | 14.6235 | 6.4861 | 1.0679 | 0.76751 | 6.4861 | 0.56343 | 4.7615 | Connections Reform
NORTHENDEN | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382555 | 390327 | 400 | 4.5726 | 8.7473 | 12.2473 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 9.31 | Connections Reform
NWGB PARTINGTON | 6.6 | CARRINGTON BSP | CARRINGTON BSP | CARRINGTON | 372569 | 392079 | 400 | 4.5726 | 2.8451 | 7.7851 | 11.2179 | 1.9575 | 1.4344 | 7.7851 | 1.4344 | 10.0382 | Connections Reform
OFFERTON | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 391010 | 389489 | 400 | 4.5726 | 1.5589 | 1.5589 | 28.9822 | 12.4589 | 9.0903 | 1.5589 | 9.1327 | 0 | Connections Reform
OPENSHAW | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 388606 | 397346 | 630 | 7.2019 | 1.5234 | 5.843 | 2.3359 | 0.40761 | 0.29869 | 2.3359 | 1.4344 | 5.886 | Connections Reform
ORMSKIRK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 341294 | 408158 | 800 | 15.242 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 10.4513 | Connections Reform
PADIHAM | 11 | PADIHAM | PADIHAM | PADIHAM | 378428 | 433238 | 400 | 7.621 | 15.9941 | 22.9941 | 6.7008 | 1.1032 | 0.79292 | 6.7008 | 0.84345 | 7.1279 | Connections Reform
PEEL ST | 11 | PADIHAM | PADIHAM | PADIHAM | 374463 | 441514 | 630 | 12.0031 | 1.879 | 11.679 | 19.6263 | 19.6263 | 19.6263 | 11.679 | 19.6031 | 8.983 | Connections Reform
PENDLETON | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381161 | 398842 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
PETTERIL BANK | 11 | CARLISLE | CARLISLE | HARKER | 341768 | 553686 | 400 | 7.621 | 4.5445 | 8.6815 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
PHILLIPS LANE | 6.6 | NELSON | NELSON | PADIHAM | 387571 | 439522 | 800 | 9.1452 | 2.4704 | 11.4704 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
PICCADILLY | 6.6 | BLOOM ST | BLOOM ST | SOUTH MANCHESTER | 384427 | 398261 | 400 | 4.5726 | 0 | 9.0028 | 30.2834 | 8.273 | 6.0362 | 9.0028 | 6.0414 | 15.0117 | Connections Reform
PIMBO | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 349148 | 404549 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 10.4513 | Connections Reform
PIRELLI | 11 | CARLISLE | CARLISLE | HARKER | 339059 | 553548 | 400 | 7.621 | 6.2477 | 11.0449 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 1.4344 | 7 | Connections Reform
PORTWOOD | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 389826 | 390619 | 400 | 4.5726 | 1.5589 | 1.5589 | 28.596 | 9.1585 | 6.6823 | 1.5589 | 6.7371 | 0 | Connections Reform
POULTON | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 335679 | 439130 | 800 | 9.1452 | 7.0012 | 8.9812 | 11.2179 | 1.9575 | 1.4344 | 8.9812 | 1.4344 | 6.9765 | Connections Reform
POYNTON | 11 | HAZEL GROVE | HAZEL GROVE | BREDBURY | 392096 | 383493 | 630 | 12.0031 | 7.0357 | 10.5357 | 22.8897 | 13.0119 | 9.3519 | 10.5357 | 9.4181 | 10.8112 | Connections Reform
PREESALL | 11 | THORNTON | THORNTON | STANAH | 336965 | 446547 | 800 | 15.242 | 13.3484 | 17.8484 | 29.788 | 12.5579 | 9.2023 | 17.8484 | 9.0987 | 15.8281 | Connections Reform
PRESTON EAST | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356777 | 432926 | 630 | 7.2019 | 0 | 0 | 2.6918 | 0.43658 | 0.31854 | 0 | 1.4344 | 0 | Connections Reform
PRESTON OLD RD | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332562 | 434929 | 800 | 9.1452 | 10.6034 | 15.2404 | 30.2892 | 11.504 | 8.3937 | 15.2404 | 8.77 | 17.138 | Connections Reform
PRESTWICH | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 381392 | 404001 | 400 | 4.5726 | 5.829 | 10.466 | 31.4025 | 7.9892 | 5.8291 | 10.466 | 5.8553 | 6.3816 | Connections Reform
PRINGLE ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 369088 | 427387 | 400 | 4.5726 | 5.6011 | 13.1611 | 29.4223 | 12.792 | 9.3334 | 13.1611 | 8.8549 | 17.2513 | Connections Reform
PRINNY HILL | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 378328 | 423395 | 630 | 7.2019 | 9.9582 | 15.0582 | 25.0372 | 10.6323 | 7.7576 | 15.0582 | 9.5083 | 14.3872 | Connections Reform
QUEENS PARK | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 385893 | 400645 | 400 | 4.5726 | 0.60394 | 4.2559 | 11.2179 | 1.9575 | 1.4344 | 4.2559 | 1.4344 | 0 | Connections Reform
RANDAL ST | 6.6 | BLACKBURN | BLACKBURN | PENWORTHAM | 368092 | 428515 | 630 | 7.2019 | 3.323 | 16.023 | 34.5907 | 12.6621 | 9.2386 | 16.023 | 8.8192 | 17.3639 | Connections Reform
RAWTENSTALL RD | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 379395 | 422143 | 630 | 7.2019 | 10.8013 | 15.4383 | 30.5998 | 15.8468 | 11.5623 | 15.4383 | 11.7382 | 14.2835 | Connections Reform
REDDISH VALE | 6.6 | VERNON PARK | VERNON PARK | BREDBURY | 390147 | 393309 | 800 | 9.1452 | 1.5589 | 1.5589 | 29.8741 | 9.8344 | 7.1754 | 1.5589 | 7.0914 | 0 | Connections Reform
RIBBLESDALE T13 & T14 | 11 | PADIHAM | PADIHAM | PADIHAM | 374759 | 443587 | 800 | 15.242 | 2.279 | 5.029 | 22.7667 | 16.27 | 11.6936 | 5.029 | 11.8923 | 1.683 | Connections Reform
RIBBLETON | 6.6 | PRESTON EAST | PRESTON EAST | PENWORTHAM | 356730 | 431506 | 630 | 7.2019 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
RINGLEY | 11 | KEARSLEY LOCAL | KEARSLEY LOCAL | KEARSLEY | 376120 | 405531 | 630 | 12.0031 | 0 | 11.7952 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
RISLEY | 11 | - | - | BOLD | 365181 | 392989 | 400 | 7.621 | 0 | 4.6708 | 8.868 | 1.4601 | 1.0494 | 4.6708 | 1.2626 | 4.1747 | N/A
ROBERT HALL ST | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 381359 | 397718 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
ROCHDALE CENTRAL | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 389111 | 413393 | 630 | 7.2019 | 22.4068 | 35.4068 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Connections Reform
ROMAN RD | 6.6 | LOWER DARWEN | LOWER DARWEN | ROCHDALE | 369058 | 426505 | 630 | 7.2019 | 3.8319 | 11.3072 | 22.6154 | 3.9463 | 2.8918 | 11.3072 | 0 | 0 | Connections Reform
ROMILEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393626 | 390716 | 400 | 7.621 | 0.064214 | 1.5589 | 22.5098 | 10.5621 | 7.5912 | 1.5589 | 7.5834 | 0 | Connections Reform
ROSSALL | 6.6 | THORNTON | THORNTON | STANAH | 331916 | 445505 | 400 | 4.5726 | 1.2521 | 4.7521 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
ROYTON | 6.6 | ROYTON | ROYTON | WHITEGATE | 392426 | 407533 | 800 | 9.1452 | 5.3712 | 14.6613 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
SALE | 6.6 | SALE | SALE | CARRINGTON | 378952 | 392177 | 630 | 7.2019 | 7.9493 | 11.5432 | 30.1984 | 8.4996 | 6.2016 | 11.5432 | 6.5677 | 14.7385 | Connections Reform
SALE MOOR | 6.6 | SALE | SALE | CARRINGTON | 379671 | 391133 | 400 | 4.5726 | 2.1265 | 2.1265 | 11.7228 | 11.7228 | 11.7228 | 2.1265 | 12.01 | 1.3941 | Connections Reform
SALFORD QUAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 380334 | 397555 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
SAMLESBURY ENTERPRISE ZONE | 11 | BLACKBURN |  | PENWORTHAM | 363416 | 431248 | 630 | 12 | 20.2086 | 27.0007 | 27.5016 | 18.0682 | 12.9859 | 27.0007
SANDGATE | 11 | BARROW & SANDGATE | BARROW | HARKER | 321492 | 468870 | 630 | 12.0031 | 10.9888 | 15.4888 | 29.7534 | 10.0677 | 7.2359 | 15.4888 | 7.2924 | 14.3266 | Connections Reform
SCARISBRICK | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 338069 | 412086 | 400 | 7.621 | 0 | 0 | 6.2775 | 1.9575 | 1.4344 | 0 | 1.4344 | 3.6656 | Connections Reform
SEBERGHAM | 11 | CARLISLE | CARLISLE | HARKER | 335344 | 542653 | 630 | 12.0031 | 0.89005 | 1.89 | 1.9632 | 1.9575 | 1.4344 | 1.89 | 1.4344 | 1.1732 | Connections Reform
SEDBERGH | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 365151 | 491747 | 400 | 7.621 | 2.615 | 12.4942 | 18.5214 | 18.5214 | 13.837 | 12.4942 | 0 | 0 | Connections Reform
SELSMIRE | 11 | PENRITH & SHAP | PENRITH | HUTTON | 361018 | 507505 | 630 | 12.0031 | 0.66085 | 0.66085 | 4.6434 | 4.6434 | 4.6434 | 0.66085 | 4.9054 | 1.1883 | Connections Reform
SETTLE | 11 | PADIHAM | PADIHAM | PADIHAM | 381588 | 463721 | 630 | 12.0031 | 0.66362 | 8.1636 | 13.8784 | 13.8784 | 13.8784 | 8.1636 | 13.3716 | 7.6618 | Connections Reform
SEVEN STARS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 352653 | 421636 | 800 | 15.242 | 0 | 3.4623 | 31.424 | 26.374 | 18.9555 | 3.4623 | 18.9995 | 5.2353 | Connections Reform
SHANNON ST SOUTH | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 330806 | 435291 | 630 | 7.2019 | 3.8711 | 10.2793 | 31.7373 | 10.7714 | 7.8591 | 10.2793 | 8.0106 | 5.397 | Connections Reform
SHAP | 11 | PENRITH & SHAP | PENRITH | HUTTON | 356910 | 513357 | 400 | 7.621 | 2.7148 | 5.5148 | 12.5332 | 12.5332 | 12.5332 | 5.5148 | 12.2325 | 7.0318 | Connections Reform
SHAW | 6.6 | ROYTON | ROYTON | WHITEGATE | 394298 | 409450 | 800 | 9.1452 | 5.3712 | 15.8789 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
Siddick | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 300289 | 530805 | 630 | 12.0031 | 13.2873 | 19.7873 | 2.6844 | 0.44197 | 0.31765 | 2.6844 | 0 | 0 | Connections Reform
SILLOTH | 11 | CARLISLE | CARLISLE | HARKER | 311307 | 553464 | 400 | 7.621 | 19.1361 | 41.3752 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
SKELMERSDALE | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347198 | 407434 | 630 | 12.0031 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.3976 | 7.809 | Connections Reform
SKELTON C | 11 | PENRITH & SHAP | PENRITH | HUTTON | 342672 | 538337 | 630 | 12.0031 | 10.2795 | 12.6267 | 21.1232 | 21.1232 | 17.1796 | 12.6267 | 17.7881 | 13.3736 | Connections Reform
SLIPWAY | 11 | EGREMONT | EGREMONT | HARKER | 297180 | 518183 | 400 | 7.621 | 4.4657 | 6.4657 | 16.3332 | 3.1754 | 2.3269 | 6.4657 | 12.7115 | 7.3459 | Connections Reform
SNIPE | 6.6 | DROYLSDEN | DROYLSDEN | STALYBRIDGE | 391844 | 398322 | 800 | 9.1452 | 8.4931 | 13.1586 | 2.3359 | 0.40761 | 0.29869 | 2.3359 | 1.4344 | 11.2179 | Connections Reform
S.E. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392001 | 372504 | 630 | 12.0031 | 2.74 | 2.74 | 11.2179 | 1.9575 | 1.4344 | 2.74 | 1.4344 | 0 | offer signed 25/04/2025
SOUTH PARK | 11 | LYTHAM | LYTHAM | PENWORTHAM | 336410 | 427512 | 400 | 7.621 | 14.1079 | 19.5725 | 21.6604 | 11.2692 | 8.0994 | 19.5725 | 0 | 0 | Connections Reform
S.W. MACCLESFIELD | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 390968 | 373004 | 400 | 7.621 | 2.74 | 2.74 | 11.2179 | 1.9575 | 1.4344 | 2.74 | 1.4344 | 0 | offer signed 25/04/2025
SPA RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 371065 | 409109 | 400 | 4.5726 | 8.5516 | 8.5516 | 11.2179 | 1.9575 | 1.4344 | 8.5516 | 1.4344 | 5.2215 | Connections Reform
SPADEADAM 132/11KV | 11 | - | - | HARKER | 361282 | 570359 | 1250 | 23.8157 | 5.77 | 7.52 | 1.6795 | 0.44197 | 0.31765 | 1.6795 | 0.31765 | 1.6795 | Connections Reform
SPOTLAND | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 387882 | 414309 | 630 | 7.2019 | 8.1507 | 11.6507 | 22.546 | 12.6571 | 9.235 | 11.6507 | 4.1691 | 9.6296 | Connections Reform
SPRING COTTAGE | 6.6 | NELSON | NELSON | PADIHAM | 385446 | 437481 | 400 | 4.5726 | 4.0155 | 17.7955 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
SPRING GARDEN ST 11kV | 11 | LANCASTER | LANCASTER | HEYSHAM | 347661 | 461494 | 800 | 15.242 | 18.1666 | 19.3919 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.5151 | 5.0572 | Connections Reform
SPRING GARDEN ST 6.6KV | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 347651 | 461484 | 800 | 9.1452 | 12.6158 | 16.7528 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.5151 | 5.0572 | Connections Reform
SQUIRES GATE | 6.6 | BLACKPOOL | BLACKPOOL | PENWORTHAM | 332037 | 432063 | 400 | 4.5726 | 9.4674 | 14.0674 | 18.3724 | 2.9797 | 2.1741 | 14.0674 | 2.1114 | 6.2955 | Connections Reform
ST ANNES | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 331716 | 429849 | 630 | 7.2019 | 10.853 | 14.353 | 21.6604 | 9.5895 | 6.9967 | 14.353 | 0 | 0 | Connections Reform
ST JOHNS | 6.6 | Frederick Road | FREDERICK RD | KEARSLEY | 383100 | 398078 | 600 | 6.8589 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0
ST MARYS | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 392582 | 405316 | 630 | 7.2019 | 8.1268 | 11.3681 | 29.5137 | 10.8997 | 7.9527 | 11.3681 | 7.7148 | 4.6017 | Connections Reform
ST MARYS ST | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 354932 | 429640 | 400 | 4.5726 | 6.9189 | 10.4189 | 11.2179 | 1.9575 | 1.4344 | 10.4189 | 1.4344 | 10.0664 | Connections Reform
ST THOMAS RD | 6.6 | LYTHAM | LYTHAM | PENWORTHAM | 332713 | 428643 | 400 | 4.5726 | 14.4111 | 19.0481 | 21.6604 | 12.7967 | 9.3368 | 19.0481 | 0 | 0 | Connections Reform
STAINBURN | 11 | STAINBURN & SIDDICK | STAINBURN | HARKER | 302535 | 529330 | 630 | 12.0031 | 8.9919 | 11.4919 | 7 | 1.9575 | 1.4344 | 7 | 0 | 0 | Connections Reform
STANDISH | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 356139 | 410059 | 630 | 12.0031 | 0 | 0 | 18.5035 | 7.0265 | 5.05 | 0 | 1.9914 | 1.9914 | Connections Reform
STRANGEWAYS | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 383780 | 399743 | 400 | 4.5726 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
STRAWBERRY BANK | 6.6 | HUNCOAT | HUNCOAT | PADIHAM | 376338 | 429396 | 630 | 7.2019 | 11.7843 | 15.9213 | 20.1283 | 3.3552 | 2.448 | 15.9213 | 2.4384 | 6.5078 | Connections Reform
STUART ST | 6.6 | STUART ST | STUART ST | STALYBRIDGE | 387190 | 398835 | 600 | 6.8589 | 2.5383 | 9.5383 | 11.2179 | 1.9575 | 1.4344 | 9.5383 | 1.4344 | 0 | Connections Reform
STUBBINS | 11 | ROSSENDALE | ROSSENDALE | PADIHAM | 379112 | 418005 | 400 | 7.621 | 7.7257 | 24.7257 | 26.0033 | 4.2812 | 3.077 | 24.7257 | 2.782 | 23.5098 | Connections Reform
SWINTON | 11 | AGECROFT | AGECROFT | KEARSLEY | 378367 | 401718 | 800 | 15.242 | 13.7271 | 18.7298 | 30.0295 | 14.9622 | 10.7536 | 18.7298 | 10.853 | 18.1986 | Connections Reform
TAME VALLEY | 6.6 | HARTSHEAD-HEYROD | HARTSHEAD-HEYROD | STALYBRIDGE | 395148 | 398108 | 630 | 7.2019 | 8.5077 | 13.1447 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
TARDY GATE | 11 | RIBBLE | RIBBLE | PENWORTHAM | 353958 | 426066 | 400 | 7.621 | 10.3338 | 14.4708 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.065 | Connections Reform
TARLETON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 344741 | 422417 | 400 | 7.621 | 0 | 0 | 16.3222 | 4.9857 | 3.5833 | 0 | 0.31765 | 2.6844 | Connections Reform
THE HEIGHT | 6.6 | AGECROFT | AGECROFT | KEARSLEY | 379792 | 400497 | 400 | 4.5726 | 4.587 | 15.287 | 29.6379 | 10.0935 | 7.3645 | 15.287 | 7.3789 | 14.5981 | Connections Reform
THORLEY LN | 11 | MOSS NOOK |  | SOUTH MANCHESTER | 381374 | 386134 | 630 | 12 | 7.6878 | 32.8878 | 11.2179 | 1.9575 | 1.4344 | 11.2179
THORNTON | 11 | BISPHAM | BISPHAM | PENWORTHAM | 334207 | 442111 | 630 | 12.0031 | 8.9964 | 12.1334 | 10.191 | 1.6779 | 1.2059 | 10.191 | 0.31765 | 2.6844 | Connections Reform
TOWNLEY ST | 11 | CHADDERTON | CHADDERTON | WHITEGATE | 387242 | 405960 | 400 | 7.621 | 4.4217 | 4.4217 | 32.1284 | 8.689 | 6.3672 | 4.4217 | 1.3649 | 0 | Connections Reform
TRAFFORD | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 380714 | 396551 | 630 | 7.2019 | 1.83 | 8.83 | 22.6463 | 8.0201 | 5.8517 | 8.83 | 5.7122 | 14.3365 | Connections Reform
TRAFFORD PARK NORTH | 6.6 | BARTON | BARTON | CARRINGTON | 378738 | 397694 | 630 | 7.2019 | 3.7038 | 8.9538 | 2.6918 | 0.43658 | 0.31854 | 2.6918 | 0.31848 | 2.6914 | Connections Reform
TRINITY | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 382649 | 398230 | 630 | 7.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Connections Reform
TULKETH | 6.6 | RIBBLE | RIBBLE | PENWORTHAM | 352393 | 431036 | 400 | 4.5726 | 9.3598 | 13.4968 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 8.4618 | Connections Reform
ULVERSTON | 11 | ULVERSTON | ULVERSTON | HARKER | 327495 | 477808 | 630 | 12.0031 | 6.1011 | 9.1011 | 15.2785 | 9.8517 | 7.0806 | 9.1011 | 7.6223 | 7.75 | Connections Reform
UNION RD | 6.6 | BOLTON | BOLTON | KEARSLEY | 372174 | 410598 | 630 | 7.2019 | 7.8001 | 12.4371 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 9.7198 | Connections Reform
UPHOLLAND | 11 | ORRELL | ORRELL | KIRKBY | 352531 | 404369 | 630 | 12.0031 | 3.6164 | 8.3747 | 23.2036 | 11.4502 | 8.2295 | 8.3747 | 8.1328 | 6.6945 | Connections Reform
URMSTON | 6.6 | STRETFORD | STRETFORD | SOUTH MANCHESTER | 377117 | 395709 | 400 | 4.5726 | 9.0253 | 14.367 | 29.3832 | 7.5773 | 5.5286 | 14.367 | 5.7691 | 14.4783 | Connections Reform
VICTORIA PARK | 6.6 | LONGSIGHT | LONGSIGHT | BREDBURY | 385373 | 395948 | 630 | 7.2019 | 0 | 0 | 27.5312 | 8.0301 | 5.859 | 0 | 4.6312 | 4.9475 | Connections Reform
WARBRECK | 6.6 | BISPHAM | BISPHAM | PENWORTHAM | 331775 | 438420 | 630 | 7.2019 | 8.3899 | 11.8899 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 10.9371 | Connections Reform
WARDLEWORTH | 6.6 | BELFIELD | BELFIELD | ROCHDALE | 390339 | 414050 | 630 | 7.2019 | 8.8246 | 13.7173 | 30.2557 | 7.9587 | 5.8069 | 13.7173 | 5.5739 | 0 | Connections Reform
WARTON | 6.6 | PEEL | PEEL | PENWORTHAM | 341290 | 428540 | 1250 | 14.2894 | 2.0211 | 2.0211 | 21.5498 | 12.8925 | 9.4067 | 2.0211 | 0 | 0 | Connections Reform
WATERHEAD | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 394942 | 405940 | 400 | 4.5726 | 11.3681 | 11.3681 | 29.3523 | 13.3359 | 9.7303 | 11.3681 | 9.344 | 4.6017 | Connections Reform
WATERSWALLOWS | 11 | BUXTON | BUXTON | STALYBRIDGE | 407734 | 375459 | 630 | 12.0031 | 0 | 0 | 29.5191 | 12.461 | 8.956 | 0 | 1.3561 | 10.6051 | Connections Reform
WEASTE | 6.6 | FREDERICK RD | FREDERICK RD | KEARSLEY | 378751 | 398897 | 800 | 9.1452 | 0 | 0 | 7 | 1.9575 | 1.4344 | 0 | 1.4344 | 0 | Connections Reform
WERNETH | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391273 | 403453 | 630 | 7.2019 | 11.3681 | 11.3681 | 29.7248 | 12.9915 | 9.4789 | 11.3681 | 8.8768 | 4.6017 | Connections Reform
WESLEY PLACE BACUP | 6.6 | ROSSENDALE | ROSSENDALE | PADIHAM | 386475 | 422130 | 400 | 4.5726 | 9.9541 | 14.5911 | 30.401 | 13.1297 | 9.5798 | 14.5911 | 10.1945 | 7.7239 | Connections Reform
WEST DIDSBURY | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 383306 | 392514 | 630 | 7.2019 | 3.7274 | 10.7274 | 11.048 | 1.9575 | 1.4344 | 10.7274 | 1.4344 | 8.6933 | Connections Reform
WESTGATE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343077 | 463204 | 630 | 7.2019 | 8.8228 | 13.4598 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.5151 | 5.0572 | Connections Reform
WESTHOUGHTON | 11 | WESTHOUGHTON | WESTHOUGHTON | KEARSLEY | 365831 | 407025 | 400 | 7.621 | 0.59038 | 5.2274 | 10.8328 | 1.7835 | 1.2819 | 5.2274 | 0.088852 | 0 | Connections Reform
WESTLINTON | 11 | CARLISLE | CARLISLE | HARKER | 339551 | 564489 | 630 | 12.0031 | 4.5845 | 7.0845 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
WHALLEY | 11 | PADIHAM | PADIHAM | PADIHAM | 373376 | 436176 | 630 | 12.0031 | 10.3 | 14.937 | 26.4684 | 7.9362 | 5.7039 | 14.937 | 5.5392 | 11.0853 | Connections Reform
WHALLEY RANGE | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 382923 | 394645 | 630 | 7.2019 | 4.0762 | 13.2132 | 11.048 | 1.9575 | 1.4344 | 11.048 | 1.4344 | 10.576 | Connections Reform
WHASSET | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 350648 | 481468 | 630 | 12.0031 | 4.9378 | 8.9378 | 21.9765 | 18.8828 | 13.837 | 8.9378 | 0 | 0 | Connections Reform
WHITTLE LE WOODS | 11 | LEYLAND | LEYLAND | PENWORTHAM | 357874 | 421203 | 630 | 12.0031 | 5.0494 | 8.5494 | 23.4528 | 14.5552 | 10.4611 | 8.5494 | 10.3146 | 9.0214 | Connections Reform
WHITWORTH | 6.6 | ROCHDALE CENTRAL | ROCHDALE CENTRAL | ROCHDALE | 388779 | 419157 | 630 | 7.2 | 5.2154 | 6.7154 | 9.9558 | 4.0292 | 2.9398 | 6.7154 | 3.1391 | 5.9064 | Connections Reform
WIGTON | 11 | CARLISLE | CARLISLE | HARKER | 325814 | 549933 | 400 | 7.621 | 0.97067 | 5.1077 | 6.6671 | 1.9575 | 1.4344 | 5.1077 | 1.4344 | 0.21045 | Connections Reform
WILLOW HEY | 11 | SKELMERSDALE | SKELMERSDALE | WASHWAY FARM | 347779 | 406066 | 400 | 7.621 | 0 | 0 | 11.2179 | 1.9575 | 1.4344 | 0 | 1.4344 | 9.682 | Connections Reform
WILLOWBANK | 6.6 | GREENHILL | GREENHILL | WHITEGATE | 391885 | 406064 | 630 | 7.2019 | 2.6486 | 7.2851 | 25.3708 | 13.1517 | 9.5958 | 7.2851 | 9.2635 | 4.6017 | Connections Reform
WILLOWHOLME | 11 | CARLISLE | CARLISLE | HARKER | 338653 | 556688 | 630 | 12.0031 | 4.4474 | 8.5844 | 7 | 1.9575 | 1.4344 | 7 | 1.4344 | 7 | Connections Reform
WILMSLOW | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 384710 | 381286 | 630 | 12.0031 | 3.8249 | 7.3249 | 11.2179 | 1.9575 | 1.4344 | 7.3249 | 1.4344 | 5.768 | Connections Reform
WINDERMERE | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 341657 | 498418 | 630 | 12.0031 | 7.179 | 13.5558 | 30.7106 | 18.8828 | 13.837 | 13.5558 | 0 | 0 | Connections Reform
WINIFRED RD | 6.6 | ADSWOOD | ADSWOOD | BREDBURY | 389971 | 388470 | 630 | 7.2019 | 3.9632 | 7.4632 | 17.4779 | 6.9465 | 5.0683 | 7.4632 | 2.1791 | 7.5047 | Connections Reform
WITHINGTON | 6.6 | WEST DIDSBURY | WEST DIDSBURY | SOUTH MANCHESTER | 384841 | 392774 | 630 | 7.2019 | 2.2457 | 5.7457 | 11.048 | 1.9575 | 1.4344 | 5.7457 | 1.4344 | 6.0832 | Connections Reform
WITHYFOLD DRIVE | 11 | MACCLESFIELD | MACCLESFIELD | MACCLESFIELD | 392132 | 374352 | 400 | 7.621 | 2.74 | 2.74 | 11.2179 | 1.9575 | 1.4344 | 2.74 | 0.31765 | 0 | offer signed 25/04/2025
WOODBINE ST | 6.6 | CASTLETON | CASTLETON | ROCHDALE | 390519 | 412388 | 800 | 9.1452 | 5.4903 | 8.9903 | 23.9427 | 14.0666 | 10.2634 | 8.9903 | 10.5673 | 8.8316 | Connections Reform
WOODFIELD RD | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 358258 | 418014 | 400 | 7.621 | 0 | 0 | 30.9563 | 13.9479 | 10.0246 | 0 | 5.1053 | 5.1053 | Connections Reform
WOODHILL LANE | 6.6 | LANCASTER | LANCASTER | HEYSHAM | 343294 | 463785 | 400 | 4.5726 | 3.1575 | 4.1575 | 11.2179 | 1.9575 | 1.4344 | 4.1575 | 1.5151 | 2.7595 | Connections Reform
WOODHOUSE PARK | 11 | MOSS NOOK | MOSS NOOK | SOUTH MANCHESTER | 382132 | 386340 | 630 | 12.0031 | 0.2042 | 3.7042 | 11.2179 | 1.9575 | 1.4344 | 3.7042 | 1.4344 | 0.86929 | Connections Reform
WOODLEY | 11 | VERNON PARK | VERNON PARK | BREDBURY | 393116 | 392019 | 400 | 7.621 | 1.5589 | 1.5589 | 10.7303 | 1.7667 | 1.2697 | 1.5589 | 1.0921 | 0 | Connections Reform
WOOLFOLD | 11 | BURY | BURY | KEARSLEY | 378874 | 411666 | 630 | 12.0031 | 11.6115 | 15.6115 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
WORDSWORTH ST | 6.6 | BOLTON | BOLTON | KEARSLEY | 370709 | 410873 | 400 | 4.5726 | 9.6965 | 14.3335 | 11.2179 | 1.9575 | 1.4344 | 11.2179 | 1.4344 | 11.2179 | Connections Reform
WORSLEY MESNES | 6.6 | WIGAN | WIGAN | KIRKBY | 357435 | 403977 | 630 | 7.2019 | 4.2143 | 12.8814 | 25.5181 | 11.9744 | 8.7368 | 12.8814 | 7.7377 | 8.7753 | Connections Reform
WRIGHTINGTON | 11 | WRIGHTINGTON | WRIGHTINGTON | PENWORTHAM | 353466 | 413290 | 400 | 7.621 | 0 | 0 | 29.7842 | 15.3476 | 11.0306 | 0 | 5.1053 | 5.1053 | Connections Reform
YEALAND | 11 | KENDAL (PARKSIDE RD) | KENDAL (PARKSIDE RD) | HUTTON | 351537 | 475934 | 630 | 12.0031 | 0.39656 | 8.3966 | 12.7306 | 12.7306 | 12.7306 | 8.3966 | 0 | 0 | Connections Reform

## 5) BSP Headroom Data
BSP Headroom
BSP | Voltage (kV) | BCA Group (GSP) | BSP Coordinates |  | Demand Headroom (MW) |  | Generation Headroom - N-0 -(MW) |  | Battery Storage Headroom N-0 -(MW)
|  |  | Easting | Northing | Firm | Non Firm | Inverter Based | Synchronous
ADSWOOD | 33 | BREDBURY | 389188 | 388310 | 20.781 | 38.781 | 141.226 | 47.1111 | 38.781 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en | Connections Reform
AGECROFT | 33 | KEARSLEY | 380345 | 401831 | 13.7271 | 25.7271 | 91.4745 | 27.6819 | 25.7271 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en | Connections Reform
ALTRINCHAM | 33 | CARRINGTON | 376380 | 389012 | 28.5328 | 46.5328 | 146.334 | 48.9341 | 46.5328 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39778%2C-2.35667z=20?hl=en | Connections Reform
ATHERTON | 33 | KEARSLEY | 366150 | 402088 | 16.8357 | 16.8357 | 124.0447 | 28.1248 | 16.8357 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51405%2C-2.51233z=20?hl=en | Connections Reform
BARROW & SANDGATE | 33 | HARKER | 319709 | 470489 | 42.0487 | 68.6685 | 66.4 | 12.046 | 66.4 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.12391%2C-3.23018z=20?hl=en | Connections Reform
BARTON | 33 | CARRINGTON | 376758 | 397174 | 20.8562 | 39.6994 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47087%2C-2.35076z=20?hl=en | Connections Reform
BELFIELD | 33 | ROCHDALE | 391033 | 413945 | 30.4611 | 30.4611 | 56.2947 | 23.9619 | 30.4611 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.62216%2C-2.13727z=20?hl=en | Connections Reform
BISPHAM | 33 | PENWORTHAM | 332328 | 439711 | 31.7656 | 31.7656 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84897%2C-3.04054z=20?hl=en | Connections Reform
BLACKBURN | 33 | PENWORTHAM | 370584 | 429294 | 31.9136 | 31.9136 | 75.5717 | 44.8805 | 31.9136 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.7592%2C-2.44764z=20?hl=en | Connections Reform
BLACKPOOL | 33 | PENWORTHAM | 330835 | 435308 | 42.3223 | 43.1623 | 125.598 | 34.9774 | 43.1623 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80944%2C-3.05179z=20?hl=en | Connections Reform
BLOOM ST | 33 | SOUTH MANCHESTER | 384221 | 397717 | 0 | 38.2367 | 149.3756 | 48.6788 | 38.2367 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47593%2C-2.23943z=20?hl=en | Connections Reform
BOLTON | 33 | KEARSLEY | 372255 | 410566 | 14.4494 | 42.4494 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59102%2C-2.42059z=20?hl=en | Connections Reform
BURNLEY | 33 | ROCHDALE | 385569 | 434469 | 60.7407 | 63.5607 | 53.7128 | 22.758 | 53.7128 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.80624%2C-2.22125z=20?hl=en | Connections Reform
BURY | 33 | KEARSLEY | 380272 | 411184 | 19.5876 | 19.5876 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5967%2C-2.29975z=20?hl=en | Connections Reform
BUXTON | 33 | STALYBRIDGE | 407769 | 375476 | 0 | 0 | 89.0157 | 45.5009 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.27596%2C-1.885z=20?hl=en | Connections Reform
CARLISLE | 33 | HARKER | 338655 | 556583 | 20.7604 | 41.9604 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.8993%2C-2.9589z=20?hl=en | Connections Reform
CARLISLE NORTH | 11 | HARKER | 338547 | 560280 | 1.344 | 18.7624 | 5.0385 | 1.4491 | 5.0385
CARRINGTON BSP | 33 | CARRINGTON | 373110 | 393020 | 9.6123 | 30.6123 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.43349%2C-2.40648z=20?hl=en | Connections Reform
CASTLETON | 33 | ROCHDALE | 388461 | 411290 | 27.0414 | 27.0414 | 88.4573 | 37.1186 | 27.0414 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.59783%2C-2.17663z=20?hl=en | Connections Reform
CHADDERTON | 33 | WHITEGATE | 389137 | 403821 | 4.4217 | 4.4217 | 47.3659 | 8.5929 | 4.4217 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en | Connections Reform
DROYLSDEN | 33 | STALYBRIDGE | 390140 | 398146 | 36.4692 | 36.4692 | 2.222 | 0.4031 | 2.222 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en | Connections Reform
EGREMONT | 33 | HARKER | 301070 | 513074 | 50.5917 | 50.5917 | 17.3098 | 3.1403 | 17.3098 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en | Connections Reform
FREDERICK RD | 33 | KEARSLEY | 381795 | 399250 | 0 | 0 | 6.7308 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49066%2C-2.27698z=20?hl=en | Connections Reform
GOLBORNE | 33 | BOLD | 360607 | 397690 | 24.1746 | 42.1746 | 51.4976 | 9.3425 | 42.1746 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.47498%2C-2.59493z=20?hl=en | N/A
GREENHILL | 33 | WHITEGATE | 393262 | 404755 | 11.3681 | 11.3681 | 109.8684 | 38.8677 | 11.3681 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53936%2C-2.10308z=20?hl=en | Connections Reform
HAZEL GROVE | 33 | BREDBURY | 391313 | 386877 | 42.0458 | 60.0458 | 131.6766 | 36.9438 | 60.0458 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.37854%2C-2.1319z=20?hl=en | Connections Reform
HARTSHEAD-HEYROD | 33 | STALYBRIDGE | 397322 | 399942 | 28.9106 | 90.9106 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.49638%2C-2.04169z=20?hl=en | Connections Reform
HUNCOAT | 33 | PADIHAM | 377997 | 431083 | 34.856 | 48.656 | 68.4546 | 21.7721 | 48.656 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.77521%2C-2.33688z=20?hl=en | Connections Reform
HYDE | 33 | STALYBRIDGE | 395522 | 395647 | 25.7835 | 25.7835 | 30.9439 | 5.6137 | 25.7835 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.45264%2C-2.07376z=20?hl=en | Connections Reform
KEARSLEY LOCAL | 33 | KEARSLEY | 376355 | 404783 | 0 | 30.7246 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en | Connections Reform
KENDAL (PARKSIDE RD) | 33 | HUTTON | 351915 | 491858 | 7.179 | 19.179 | 60.2511 | 18.6739 | 19.179 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en | Connections Reform
LANCASTER | 33 | HEYSHAM | 348644 | 463628 | 19.3919 | 19.3919 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en | Connections Reform
LEYLAND | 33 | PENWORTHAM | 354121 | 423373 | 12.8265 | 27.7905 | 128.4578 | 33.7681 | 27.7905 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en | Connections Reform
LONGSIGHT | 33 | BREDBURY | 385592 | 396016 | 0 | 18.789 | 148.9806 | 39.185 | 18.789 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en | Connections Reform
LOWER DARWEN | 33 | ROCHDALE | 369695 | 424981 | 9.4116 | 59.4116 | 21.5122 | 3.9027 | 21.5122 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en | Connections Reform
LYTHAM | 33 | PENWORTHAM | 335361 | 429316 | 20.3574 | 20.3574 | 21.6604 | 21.6604 | 20.3574 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en | Connections Reform
MACCLESFIELD | 33 | MACCLESFIELD | 392047 | 374564 | 2.74 | 2.74 | 10.6707 | 1.9358 | 2.74 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en | offer signed 25/04/2025
MOSS NOOK | 33 | SOUTH MANCHESTER | 384073 | 385068 | 7.6878 | 32.8878 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en | Connections Reform
NELSON | 33 | PADIHAM | 385989 | 438643 | 10.0813 | 31.4941 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.84299%2C-2.214z=20?hl=en | Connections Reform
NEW MILLS | 33 | STALYBRIDGE | 401141 | 383916 | 20.3674 | 20.3674 | 47.4136 | 47.4136 | 20.3674 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.35237%2C-1.9844z=20?hl=en | Connections Reform
ORRELL | 33 | KIRKBY | 352784 | 404565 | 3.6164 | 60.6164 | 135.7877 | 52.8146 | 60.6164 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.5356%2C-2.71374z=20?hl=en | Connections Reform
PADIHAM | 33 | PADIHAM | 378571 | 433224 | 24.6331 | 56.1331 | 140.353 | 30.754 | 56.1331 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79502%2C-2.32919z=20?hl=en | Connections Reform
PEEL | 33 | PENWORTHAM | 335644 | 432080 | 2.0211 | 2.0211 | 21.5498 | 21.5498 | 2.0211 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.78114%2C-2.9776z=20?hl=en | Connections Reform
PENRITH & SHAP | 33 | HUTTON | 349996 | 530398 | 12.6267 | 12.6267 | 21.1232 | 21.1232 | 12.6267 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66637%2C-2.77723z=20?hl=en | Connections Reform
PRESTON EAST | 33 | PENWORTHAM | 356774 | 432942 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.79104%2C-2.6584z=20?hl=en | Connections Reform
RED BANK | 33 | WHITEGATE | 384542 | 399276 | 25.4692 | 43.4692 | 152.5583 | 32.6283 | 43.4692
RADCLIFFE | 11 | KEARSLEY | 377524 | 406160 | 0 | 0 | 44.3575 | 38.6584 | 0
RIBBLE | 33 | PENWORTHAM | 351794 | 429241 | 75.3246 | 111.3246 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75725%2C-2.73184z=20?hl=en | Connections Reform
ROCHDALE CENTRAL | 33 | ROCHDALE | 389111 | 413393 | 46.5154 | 58.5154 | 83.1391 | 22.1482 | 58.5154 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61653%2C-2.16602z=20?hl=en | Connections Reform
ROSSENDALE | 33 | PADIHAM | 380261 | 422010 | 35.8424 | 48.7112 | 84.4355 | 45.5562 | 48.7112 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.69402%2C-2.30041z=20?hl=en | Connections Reform
ROYTON | 33 | WHITEGATE | 392426 | 407533 | 5.3712 | 71.784 | 0 | 0 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56464%2C-2.11572z=20?hl=en | Connections Reform
SALE | 33 | CARRINGTON | 378726 | 392892 | 7.9493 | 11.5432 | 78.0965 | 48.9947 | 11.5432 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42581%2C-2.31835z=20?hl=en | Connections Reform
SKELMERSDALE | 33 | WASHWAY FARM | 347172 | 407455 | 0 | 0 | 10.6707 | 1.9358 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.56076%2C-2.79859z=20?hl=en | Connections Reform
STAINBURN & SIDDICK | 33 | HARKER | 302535 | 529330 | 20.8714 | 69.4194 | 6.7308 | 1.9358 | 6.7308 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.66252%2C-3.54717z=20?hl=en | Connections Reform
STRETFORD | 33 | SOUTH MANCHESTER | 380069 | 395104 | 9.0253 | 41.2763 | 134.3787 | 34.9978 | 41.2763 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4523%2C-2.30113z=20?hl=en | Connections Reform
STUART ST | 33 | STALYBRIDGE | 387247 | 398875 | 51.2446 | 114.2446 | 10.6707 | 1.9358 | 10.6707 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.48612%2C-2.19476z=20?hl=en | Connections Reform
THORNTON | 33 | STANAH | 334559 | 443368 | 25.7147 | 37.7147 | 36.2039 | 12.419 | 36.2039 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.8709%2C-3.00229z=20?hl=en | Connections Reform
TRIMPELL | 11 | HEYSHAM | 341861 | 458979 | 9.4981 | 9.4981 | 5.0385 | 1.4491 | 5.0385
ULVERSTON | 33 | HARKER | 327495 | 477808 | 67.4186 | 67.4186 | 65.5616 | 27.7814 | 65.5616 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.1907%2C-3.11215z=20?hl=en | Connections Reform
VERNON PARK | 33 | BREDBURY | 391131 | 390929 | 1.5589 | 1.5589 | 84.8416 | 15.8765 | 1.5589 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.41552%2C-2.13492z=20?hl=en | Connections Reform
WEST DIDSBURY | 33 | SOUTH MANCHESTER | 382900 | 393269 | 11.7335 | 48.2335 | 10.6231 | 1.9358 | 10.6231 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.42927%2C-2.25292z=20?hl=en | Connections Reform
WESTHOUGHTON | 33 | KEARSLEY | 365831 | 407025 | 25.2761 | 25.2761 | 89.5308 | 24.4243 | 25.2761 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.55846%2C-2.51787z=20?hl=en | Connections Reform
WIGAN | 33 | KIRKBY | 358343 | 404626 | 4.2143 | 43.2143 | 113.2768 | 63.2894 | 43.2143 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53645%2C-2.62967z=20?hl=en | Connections Reform
WRIGHTINGTON | 33 | PENWORTHAM | 354460 | 413610 | 0 | 0 | 67.654 | 18.8119 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.61411%2C-2.70439z=20?hl=en | Connections Reform

## 6) GSP Demand Headroom Data (hidden)
GSP Headroom
Substation | GSP | Voltage (kV) | GSP Group | GSP Coordinates |  | Demand Headroom (MVA) |  | Battery Storage Headroom N-0 -(MW)
|  |  |  | Easting | Northing | Firm (non inverter based) | Non Firm (inverter based)
Bold GSP (132) | BOLD | 132 | BOLD | 353959 | 393258 | -139.0585 | -139.0585 | -99.1396 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.39156%2C-2.16403z=20?hl=en
Bredbury (132) | BREDBURY | 132 | BREDBURY | 391365 | 390944 | 130.6602 | 146.7402 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.51279%2C-2.29754z=20?hl=en
Carrington GSP (132) | CARRINGTON | 132 | CARRINGTON | 372952 | 393301 | -48.4123 | 104.5877 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53127%2C-2.16481z=20?hl=en
Harker / Hutton GSP (132) | Harker ENWL SGTs 1 2 3A 4 / Hutton GSP GROUP | 132 | HARKER / HUTTON | 338285 | 561159 | -654.416 | -654.416 | -1393.5411 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.4802%2C-2.14954z=20?hl=en
Heysham GSP (132) | HEYSHAM | 132 | HEYSHAM | 341889 | 460007 | 328.4761 | 328.4761 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.50354%2C-3.52919z=20?hl=en
Kearsley GSP (132) | KEARSLEY | 132 | KEARSLEY | 376283 | 404800 | -9.6464 | 127.5736 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.53905%2C-2.35884z=20?hl=en
Padiham (132) | PADIHAM | 132 | PADIHAM | 378522 | 433196 | -252.3064 | -252.3064 | -271.5158 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.31969%2C-2.74168z=20?hl=en
Penwortham East / Rochdale SGT 1 GSP (132) | PENWORTHAM EAST/ROCHDALE | 132 | PENWORTHAM EAST / ROCHDALE | 350213 | 428032 | 323.9712 | 342.7211 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=54.06622%2C-2.78639z=20?hl=en
Penwortham West / Stanah GSP (132) | PENWORTHAM WEST/STANAH | 132 | PENWORTHAM WEST / STANAH | 350200 | 428029 | 234.1023 | 234.1023 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.70478%2C-2.69663z=20?hl=en
Rochdale GSP (132) | ROCHDALE | 132 | ROCHDALE | 385789 | 413832 | 131.1469 | 131.1469 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.46086%2C-2.21901z=20?hl=en
South Manchester GSP (132) | SOUTH MANCHESTER | 132 | SOUTH MANCHESTER | 381823 | 391734 | 187.0908 | 187.0908 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.72038%2C-2.45999z=20?hl=en
Stalybridge GSP (132) | STALYBRIDGE | 132 | STALYBRIDGE | 397172 | 399496 | 77.1566 | 174.0566 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.75633%2C-2.98215z=20?hl=en
Washway Farm / Kirkby GSP (132) | Washway Farm GSP / Kirkby GSP GROUP | 132 | WASHWAY FARM / KIRKBY | 345822 | 407637 | -106.5126 | -106.5126 | -15.7832 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.26811%2C-2.12063z=20?hl=en
Whitegate GSP (132) | WHITEGATE | 132 | WHITEGATE | 389202 | 403745 | 175.4843 | 279.2843 | 0 | https://www.google.com/maps/d/viewer?mid=1wLVvNAtxF44PseqlxB-yZb4QiTLsY0T8&ll=53.36201%2C-2.2408z=20?hl=en

## 7)Transmission Capacity - App G
Appendix G Summary
GSP / Site |  | Capacity of Connected & Contracted Connections (MW) |  |  |  | Materiality Headroom (Part 5) (MW) | Materiality Status | Capacity in Project Progression / Modification Application | Total Aggregated Developer Capacity Limit(MW) | Transmission FL Headroom (kA) | Project Progression Update
|  | Part 1 | Part 2 | Part 3 | Part 4
BOLD* | BOLD | 25.1 | 50.4 | 0 | 0 | N/A | B | N/A | 75.5 | 0 | N/A
BREDBURY | BREDBURY | 10.1 | 124.2 | 0 | 280.6 | 0 | C | 0 | 414.9 | 3 | Connections Reform
CARRINGTON | CARRINGTON | 105 | 94 | 0 | 4 | 0 | C | 0 | 203 | 5.13 | Connections Reform
HARKER | HARKER | 765.4 | 40 | 0 | 916.8 | 0 | D | 0 | 1722.2 | 0 | Connections Reform
HUTTON | HUTTON | 47.9 | 48 | 0 | 139 | 0 | D | 0 | 234.9 | 0 | Connections Reform
HEYSHAM | HEYSHAM | 292.6 | 0 | 75 | 21.5 | 0 | C | 24 | 389.1 | 0 | Connections Reform
KEARSLEY | KEARSLEY | 57.9 | 229.7 | 11 | 35 | 0 | C | 0 | 333.6 | 3 | Connections Reform
KIRKBY | KIRKBY | 6 | 86.3 | 0 | 80.9 | 0 | D | 0 | 173.2 | 3 | Connections Reform
MACCLESFIELD | MACCLESFIELD | 27.9 | 20 | 0 | 7.5 | 0 | C | 0 | 55.4 | 3 | offer signed 25/04/2025
PADIHAM | PADIHAM | 35.5 | 128.1 | 149.9 | 193.9 | 0 | D | 0 | 555.4 | TBC | Connections Reform
PENWORTHAM | PENWORTHAM | 187.9 | 497.1 | 67.6 | 109.2 | 0 | D | 0 | 861.8 | 3 | Connections Reform
ROCHDALE | ROCHDALE | 204.1 | 179.1 | 35 | 376.2 | 0 | C | 0 | 794.4 | 1.92 | Connections Reform
SOUTH MANCHESTER | SOUTH MANCHESTER | 22.2 | 81.3 | 0 | 649.7 | 0 | C | 0 | 753.2 | 0 | Connections Reform
STALYBRIDGE | STALYBRIDGE | 28.3 | 226.8 | 0 | 50 | 0 | C | 0 | 305.1 | 0.591 | Connections Reform
STANAH | STANAH | 195.9 | 122.5 | 0 | 50 | 0 | C | 0 | 387.9 | 3.01 | Connections Reform
WASHWAY FARM | WASHWAY FARM | 7.9 | 101.2 | 0 | 2 | 0 | D | 0 | 111.1 | 3 | Connections Reform
WHITEGATE | WHITEGATE | 32 | 198.3 | 0 | 126.9 | 0 | C | 0 | 357.2 | 3.09 | Connections Reform
Disclaimer | Process |  |  |  | Parts 1 - 5 |  |  |  |  | Materiality Status
Note that the capacities reported in the table above were true prior to the ongoing Connections Reform, hence only indicative. SP ENW will update the table after Connections Reform, likely in Q1 (2027). | The Appendix G process aims to improve on the Statement of Works process by reducing timescales and facilitating greater transparency to the customer. Seventeen of ENWLs twenty GSPs have already converted to the Appendix G process and work is in progress to convert the three remaining sites. The above table summarises the Appendix G results of the GSPs which have already been converted from the Statement of Works process. Sites marked with an asterisk (*) are connected to the transmission network through the distribution network operated by SP Energy Networks. Appendix G submissions for these sites are made by SP Energy Networks on behalf of Electricity North West. For Further information on how to interpret the information presented in this table please refer to the user guide embedded within the first tab of this workbook. |  |  |  | Appendix G consists of 5 parts: • Part 1 – Existing power stations already connected to our network. • Part 2 – Power stations connected or contracted to connect to our network for which site specific requirements will apply e.g. power factor and controllability. • Part 3 – Power stations connected or contracted to connect to our network for which interim restrictions on availability will apply. Site specific requirements e.g. power factor and controllability, will also apply. • Part 4 – Power stations contracted to connect to our network which are unable to connect until transmission works have been completed. • Part 5 – Materiality headroom. This is a figure, determined by the transmission system operator, representing the available thermal capacity at the transmission system interface before a Modification Application is triggered. |  |  |  |  | To aid understanding we have given each GSP a materiality status. The three status are: A. The latest Appendix G return indicates that there is spare transmission system capacity at this location. B. There is insufficient capacity to accommodate any further sites without undertaking transmission system work. To identify the scope of these works a Modification Application will be required. C. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New sites may still require a new Modification Application. D. There is insufficient capacity to accommodate any further connections without undertaking work on the transmission system. These works have already been identified and there are sites in project progression. New GSPs have now been trigged by the latest Project progression return by NESO.